## 0030
Detailed results
Generated at: | 10/07/2026 22:33:52
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3786
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA/[BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00110 | RO | RIERN22 _generator | 0 | 200 |  |  | 200 | 1 |  | 200 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 53 |  | 389 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 26 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 58 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 1 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 9 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 0 | 170 |  | 170 | 0 | TRUE | FALSE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 340 | 322 |  | 340 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 7 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 11 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 7 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 15 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 6 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 12 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 6 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 12 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 11 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 12 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 4 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 1 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 1 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 11 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 17 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 22 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 3 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 3 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 10 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 30 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 11 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 9 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 26 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 0 | 96 |  | 96 | 0 | TRUE | FALSE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 0 | 58 |  | 58 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1994 | 2000 | -6 | 100 | -1369 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1994 | 2000 | -6 | 100 | 1399 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1981 | 2000 | -19 | 99 | 1391 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1981 | 2000 | -19 | 99 | -1357 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1960 | 1995 | -35 | 98 | 1383 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1910 | 1995 | -85 | 96 | 1343 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1907 | 1995 | -88 | 96 | 1351 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1907 | 1995 | -88 | 96 | 1346 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1891 | 1995 | -104 | 95 | 1332 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 946 | 999 | -53 | 95 | 367 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1873 | 1995 | -122 | 94 | 1325 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1857 | 1995 | -138 | 93 | 1311 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1832 | 1995 | -163 | 92 | 1294 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1830 | 1995 | -165 | 92 | 1293 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1824 | 1995 | -171 | 91 | 1289 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1823 | 1995 | -172 | 91 | 1288 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1823 | 1995 | -172 | 91 | 1288 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1802 | 1995 | -193 | 90 | 1275 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1801 | 1995 | -194 | 90 | 1272 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1293 | 1570 | -277 | 82 | 910 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1293 | 1570 | -277 | 82 | 910 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1624 | 1995 | -371 | 81 | 1138 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1614 | 1995 | -381 | 81 | 1132 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1267 | 1570 | -303 | 81 | 888 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1267 | 1570 | -303 | 81 | 888 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1265 | 1570 | -305 | 81 | 891 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1227 | 1570 | -343 | 78 | 863 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1216 | 1570 | -354 | 77 | 856 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1216 | 1570 | -354 | 77 | 855 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1215 | 1570 | -355 | 77 | 855 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1201 | 1570 | -369 | 77 | 845 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1197 | 1570 | -373 | 76 | 840 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1195 | 1570 | -375 | 76 | 841 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1182 | 1570 | -388 | 75 | 832 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1166 | 1570 | -404 | 74 | 819 | AC

## 0130
Detailed results
Generated at: | 10/07/2026 22:33:52
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3860
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA/[BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1918 | 2000 | -82 | 96 | -1320 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1918 | 2000 | -82 | 96 | 1347 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1905 | 2000 | -95 | 95 | 1340 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1905 | 2000 | -95 | 95 | -1308 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1841 | 1995 | -154 | 92 | 1295 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1837 | 1995 | -158 | 92 | 1302 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1827 | 1995 | -168 | 92 | 1286 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1822 | 1995 | -173 | 91 | 1285 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1807 | 1995 | -188 | 91 | 1279 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1797 | 1995 | -198 | 90 | 1268 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1403 | 1570 | -167 | 89 | 978 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1403 | 1570 | -167 | 89 | 978 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1768 | 1995 | -227 | 89 | 1248 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1761 | 1995 | -234 | 88 | 1244 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1755 | 1995 | -240 | 88 | 1240 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1744 | 1995 | -251 | 87 | 1232 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1743 | 1995 | -252 | 87 | 1231 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1738 | 1995 | -257 | 87 | 1227 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1732 | 1995 | -263 | 87 | 1225 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1362 | 1570 | -208 | 87 | 941 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1362 | 1570 | -208 | 87 | 941 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1722 | 1995 | -273 | 86 | 1216 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1342 | 1570 | -228 | 86 | 934 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1333 | 1570 | -237 | 85 | 924 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1312 | 1570 | -258 | 84 | 912 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1307 | 1570 | -263 | 83 | 907 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1306 | 1570 | -264 | 83 | 908 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1304 | 1570 | -266 | 83 | 906 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1301 | 1570 | -269 | 83 | 904 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1284 | 1570 | -286 | 82 | 894 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1266 | 1570 | -304 | 81 | 883 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1262 | 1570 | -308 | 80 | 877 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1552 | 1995 | -443 | 78 | 1087 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1543 | 1995 | -452 | 77 | 1082 | AC

## 0230
Detailed results
Generated at: | 10/07/2026 22:33:52
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3842
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA/[BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1911 | 2000 | -89 | 96 | -1315 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1911 | 2000 | -89 | 96 | 1343 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1898 | 2000 | -102 | 95 | -1303 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1898 | 2000 | -102 | 95 | 1335 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1835 | 1995 | -160 | 92 | 1292 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1832 | 1995 | -163 | 92 | 1299 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1822 | 1995 | -173 | 91 | 1284 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1816 | 1995 | -179 | 91 | 1281 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1803 | 1995 | -192 | 90 | 1276 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1410 | 1570 | -160 | 90 | 973 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1410 | 1570 | -160 | 90 | 973 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1792 | 1995 | -203 | 90 | 1265 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1762 | 1995 | -233 | 88 | 1244 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1758 | 1995 | -237 | 88 | 1243 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1751 | 1995 | -244 | 88 | 1238 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1739 | 1995 | -256 | 87 | 1229 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1738 | 1995 | -257 | 87 | 1229 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1367 | 1570 | -203 | 87 | 937 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1367 | 1570 | -203 | 87 | 937 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1733 | 1995 | -262 | 87 | 1225 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1727 | 1995 | -268 | 87 | 1222 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1351 | 1570 | -219 | 86 | 930 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1716 | 1995 | -279 | 86 | 1213 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1342 | 1570 | -228 | 85 | 920 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1321 | 1570 | -249 | 84 | 909 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1318 | 1570 | -252 | 84 | 905 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1315 | 1570 | -255 | 84 | 904 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1314 | 1570 | -256 | 84 | 903 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1309 | 1570 | -261 | 83 | 900 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1292 | 1570 | -278 | 82 | 889 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1275 | 1570 | -295 | 81 | 876 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1272 | 1570 | -298 | 81 | 877 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1548 | 1995 | -447 | 78 | 1085 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1539 | 1995 | -456 | 77 | 1080 | AC

## 0330
Detailed results
Generated at: | 10/07/2026 22:33:53
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3846
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA/[BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1901 | 2000 | -99 | 95 | -1309 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1901 | 2000 | -99 | 95 | 1336 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1889 | 2000 | -111 | 94 | 1329 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1889 | 2000 | -111 | 94 | -1297 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1834 | 1995 | -161 | 92 | 1291 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1830 | 1995 | -165 | 92 | 1298 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1822 | 1995 | -173 | 91 | 1284 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1806 | 1995 | -189 | 91 | 1274 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1804 | 1995 | -191 | 90 | 1278 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1418 | 1570 | -152 | 90 | 979 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1418 | 1570 | -152 | 90 | 979 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1786 | 1995 | -209 | 90 | 1261 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1764 | 1995 | -231 | 88 | 1248 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1762 | 1995 | -233 | 88 | 1244 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1750 | 1995 | -245 | 88 | 1238 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1377 | 1570 | -193 | 88 | 945 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1377 | 1570 | -193 | 88 | 945 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1738 | 1995 | -257 | 87 | 1229 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1570 | -205 | 87 | 941 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1735 | 1995 | -260 | 87 | 1226 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1732 | 1995 | -263 | 87 | 1224 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1728 | 1995 | -267 | 87 | 1223 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1352 | 1570 | -218 | 86 | 928 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1713 | 1995 | -282 | 86 | 1211 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1328 | 1570 | -242 | 85 | 913 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1327 | 1570 | -243 | 85 | 914 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1323 | 1570 | -247 | 84 | 911 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1323 | 1570 | -247 | 84 | 909 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1317 | 1570 | -253 | 84 | 906 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1301 | 1570 | -269 | 83 | 896 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1283 | 1570 | -287 | 82 | 883 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1281 | 1570 | -289 | 82 | 885 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1548 | 1995 | -447 | 78 | 1085 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1539 | 1995 | -456 | 77 | 1080 | AC

## 0430
Detailed results
Generated at: | 10/07/2026 22:33:53
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3840
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA/[BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1894 | 2000 | -106 | 95 | 1331 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1894 | 2000 | -106 | 95 | -1304 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1882 | 2000 | -118 | 94 | 1324 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1882 | 2000 | -118 | 94 | -1293 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1843 | 1995 | -152 | 92 | 1298 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1839 | 1995 | -156 | 92 | 1305 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1835 | 1995 | -160 | 92 | 1294 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1818 | 1995 | -177 | 91 | 1288 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1809 | 1995 | -186 | 91 | 1276 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1415 | 1570 | -155 | 90 | 975 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1415 | 1570 | -155 | 90 | 975 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1797 | 1995 | -198 | 90 | 1269 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1788 | 1995 | -207 | 90 | 1265 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1781 | 1995 | -214 | 89 | 1258 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1764 | 1995 | -231 | 88 | 1248 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1752 | 1995 | -243 | 88 | 1239 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1373 | 1570 | -197 | 87 | 940 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1373 | 1570 | -197 | 87 | 940 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1741 | 1995 | -254 | 87 | 1231 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1741 | 1995 | -254 | 87 | 1233 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1740 | 1995 | -255 | 87 | 1231 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1359 | 1570 | -211 | 87 | 936 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1719 | 1995 | -276 | 86 | 1215 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1347 | 1570 | -223 | 86 | 923 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1324 | 1570 | -246 | 84 | 910 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1324 | 1570 | -246 | 84 | 908 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1319 | 1570 | -251 | 84 | 907 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1319 | 1570 | -251 | 84 | 905 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1314 | 1570 | -256 | 84 | 902 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1298 | 1570 | -272 | 83 | 893 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1281 | 1570 | -289 | 82 | 880 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1277 | 1570 | -293 | 81 | 881 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1562 | 1995 | -433 | 78 | 1096 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1553 | 1995 | -442 | 78 | 1091 | AC

## 0530
Detailed results
Generated at: | 10/07/2026 22:33:53
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3916
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA/[BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00110 | RO | RIERN22 _generator | 0 | 200 |  |  | 200 | 19 |  | 200 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 29 |  | 389 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 0 | 114 |  | 114 | 0 | TRUE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 1 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 25 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 0 | 170 |  | 170 | 0 | TRUE | FALSE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 118 | 28 |  | 118 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 6 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 10 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 6 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 13 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 5 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 10 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 5 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 10 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 9 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 11 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 4 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 1 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 1 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 6 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 15 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 19 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 8 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 27 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 7 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 11 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 10 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 8 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 23 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 0 | 96 |  | 96 | 0 | TRUE | FALSE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 0 | 58 |  | 58 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 2 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 3 | 29 |  | 29 | 0 | FALSE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 2 | 27 |  | 27 | 0 | FALSE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 4 | 52 |  | 52 | 0 | FALSE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1998 | 2000 | -2 | 100 | -1373 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1998 | 2000 | -2 | 100 | 1403 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1985 | 2000 | -15 | 99 | -1360 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1985 | 2000 | -15 | 99 | 1395 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1951 | 1995 | -44 | 98 | 1377 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1949 | 1995 | -46 | 98 | 1373 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1944 | 1995 | -51 | 97 | 1379 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1942 | 1995 | -53 | 97 | 1370 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1926 | 1995 | -69 | 97 | 1364 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1925 | 1995 | -70 | 96 | 1360 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1902 | 1995 | -93 | 95 | 1344 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1879 | 1995 | -116 | 94 | 1329 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1874 | 1995 | -121 | 94 | 1325 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1863 | 1995 | -132 | 93 | 1318 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1853 | 1995 | -142 | 93 | 1310 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1848 | 1995 | -147 | 93 | 1308 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1845 | 1995 | -150 | 92 | 1305 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1841 | 1995 | -154 | 92 | 1302 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1401 | 1570 | -169 | 89 | 951 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1401 | 1570 | -169 | 89 | 951 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1366 | 1570 | -204 | 87 | 921 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1366 | 1570 | -204 | 87 | 921 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1362 | 1570 | -208 | 87 | 923 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1320 | 1570 | -250 | 84 | 892 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1319 | 1570 | -251 | 84 | 891 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1317 | 1570 | -253 | 84 | 890 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1315 | 1570 | -255 | 84 | 889 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1664 | 1995 | -331 | 83 | 1167 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1655 | 1995 | -340 | 83 | 1162 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1302 | 1570 | -268 | 83 | 879 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1293 | 1570 | -277 | 82 | 873 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1289 | 1570 | -281 | 82 | 866 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1281 | 1570 | -289 | 82 | 865 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1260 | 1570 | -310 | 80 | 844 | AC

## 0630
Detailed results
Generated at: | 10/07/2026 22:33:53
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3550.23
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1572 | 1570 | 2 | 100 | 1072 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1520 | 1570 | -50 | 97 | 1032 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1520 | 1570 | -50 | 97 | 1032 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1516 | 1570 | -54 | 97 | 1031 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1516 | 1570 | -54 | 97 | 1031 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1483 | 1570 | -87 | 94 | 1006 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1480 | 1570 | -90 | 94 | 1003 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1468 | 1570 | -102 | 94 | 995 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1460 | 1570 | -110 | 93 | 991 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1454 | 1570 | -116 | 93 | 987 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1436 | 1570 | -134 | 92 | 975 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1436 | 1570 | -134 | 91 | 974 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1433 | 1570 | -137 | 91 | 973 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1416 | 1570 | -154 | 90 | 957 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1728 | 1995 | -267 | 87 | 1219 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1722 | 1995 | -273 | 86 | 1219 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1720 | 1995 | -275 | 86 | 1214 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1714 | 1995 | -281 | 86 | 1211 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1684 | 1995 | -311 | 84 | 1184 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1675 | 1995 | -320 | 84 | 1180 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1675 | 1995 | -320 | 84 | 1188 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1664 | 1995 | -331 | 83 | 1178 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1660 | 1995 | -335 | 83 | 1174 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1648 | 1995 | -347 | 83 | 1165 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1635 | 1995 | -360 | 82 | 1156 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1635 | 1995 | -360 | 82 | 1155 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1621 | 1995 | -374 | 81 | 1146 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1613 | 1995 | -382 | 81 | 1141 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1584 | 2000 | -416 | 79 | 1116 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1584 | 2000 | -416 | 79 | -1097 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1575 | 2000 | -425 | 79 | -1088 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1575 | 2000 | -425 | 79 | 1110 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1491 | 1995 | -504 | 75 | 1049 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1484 | 1995 | -511 | 74 | 1045 | AC

## 0730
Detailed results
Generated at: | 10/07/2026 22:33:53
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2434.46
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1580 | 1570 | 10 | 101 | 1115 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1570 | -127 | 92 | 1018 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1570 | -127 | 92 | 1018 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1425 | 1570 | -145 | 91 | 1003 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1424 | 1570 | -146 | 91 | 1008 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1394 | 1570 | -176 | 89 | 983 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1570 | -188 | 88 | 977 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1379 | 1570 | -191 | 88 | 975 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1367 | 1570 | -203 | 87 | 967 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1362 | 1570 | -208 | 87 | 963 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1362 | 1570 | -208 | 87 | 963 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1349 | 1570 | -221 | 86 | 955 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1348 | 1570 | -222 | 86 | 953 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1342 | 1570 | -228 | 85 | 949 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1427 | 1995 | -568 | 72 | 1009 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1407 | 1995 | -588 | 71 | 992 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1398 | 1995 | -597 | 70 | 985 | AC

## 0830
Detailed results
Generated at: | 10/07/2026 22:33:53
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 1400.73
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1585 | 1570 | 15 | 101 | 1116 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1316 | 1570 | -254 | 84 | 932 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1312 | 1570 | -258 | 84 | 922 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1311 | 1570 | -259 | 83 | 925 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1311 | 1570 | -259 | 83 | 925 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1279 | 1570 | -291 | 81 | 904 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1278 | 1570 | -292 | 81 | 901 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1253 | 1570 | -317 | 80 | 886 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1238 | 1570 | -332 | 79 | 876 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1234 | 1570 | -336 | 79 | 874 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1221 | 1570 | -349 | 78 | 865 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1208 | 1570 | -362 | 77 | 855 | AC

## 0930
Detailed results
Generated at: | 10/07/2026 22:33:53
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 1590.9
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1587 | 1570 | 17 | 101 | 1123 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1335 | 1570 | -235 | 85 | 943 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1334 | 1570 | -236 | 85 | 947 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1334 | 1570 | -236 | 85 | 947 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1330 | 1570 | -240 | 85 | 945 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1296 | 1570 | -274 | 83 | 920 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1287 | 1570 | -283 | 82 | 913 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1269 | 1570 | -301 | 81 | 902 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1251 | 1570 | -319 | 80 | 889 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1247 | 1570 | -323 | 79 | 887 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1239 | 1570 | -331 | 79 | 882 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1227 | 1570 | -343 | 78 | 873 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1137 | 1570 | -433 | 72 | 810 | AC

## 1030
Detailed results
Generated at: | 10/07/2026 22:33:53
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3376.54
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1575 | 1570 | 5 | 100 | 1121 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1503 | 1570 | -67 | 96 | 1070 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1503 | 1570 | -67 | 96 | 1070 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1570 | -104 | 93 | 1044 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1458 | 1570 | -112 | 93 | 1039 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1458 | 1570 | -112 | 93 | 1039 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1456 | 1570 | -114 | 93 | 1038 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1432 | 1570 | -138 | 91 | 1020 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1429 | 1570 | -141 | 91 | 1019 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1429 | 1570 | -141 | 91 | 1018 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1798 | 1995 | -197 | 90 | 1272 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1413 | 1570 | -157 | 90 | 1007 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1784 | 1995 | -211 | 89 | 1261 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1402 | 1570 | -168 | 89 | 1000 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1401 | 1570 | -169 | 89 | 1000 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1760 | 1995 | -235 | 88 | 1242 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1379 | 1570 | -191 | 88 | 982 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1751 | 1995 | -244 | 88 | 1235 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1688 | 1995 | -307 | 85 | 1193 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1681 | 1995 | -314 | 84 | 1181 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1675 | 1995 | -320 | 84 | 1183 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1674 | 1995 | -321 | 84 | 1178 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1669 | 1995 | -326 | 84 | 1183 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1667 | 1995 | -328 | 84 | 1178 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1646 | 1995 | -350 | 82 | 1162 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1632 | 1995 | -363 | 82 | 1153 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1626 | 1995 | -369 | 82 | 1149 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1611 | 1995 | -384 | 81 | 1137 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1529 | 1995 | -466 | 77 | 1076 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1522 | 1995 | -473 | 76 | 1073 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1473 | 2000 | -527 | 74 | 1036 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1473 | 2000 | -527 | 74 | -1020 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1463 | 2000 | -537 | 73 | 1031 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1463 | 2000 | -537 | 73 | -1012 | AC

## 1130
Detailed results
Generated at: | 10/07/2026 22:33:53
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3888
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1974 | 1995 | -21 | 99 | 1397 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1954 | 1995 | -41 | 98 | 1381 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1924 | 1995 | -71 | 96 | 1358 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1916 | 1995 | -79 | 96 | 1351 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1902 | 1995 | -93 | 95 | 1338 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1897 | 1995 | -98 | 95 | 1336 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1893 | 1995 | -102 | 95 | 1341 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1885 | 1995 | -110 | 94 | 1333 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1875 | 1995 | -120 | 94 | 1326 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1858 | 1995 | -137 | 93 | 1313 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1442 | 1570 | -128 | 92 | 1031 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1442 | 1570 | -128 | 92 | 1031 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1435 | 1570 | -135 | 91 | 1026 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1435 | 1570 | -135 | 91 | 1026 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1819 | 1995 | -176 | 91 | 1285 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1819 | 1995 | -176 | 91 | 1285 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1788 | 1995 | -207 | 90 | 1263 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1403 | 1570 | -167 | 89 | 1003 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1400 | 1570 | -170 | 89 | 1001 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1570 | -178 | 89 | 995 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1773 | 2000 | -227 | 89 | 1245 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1773 | 2000 | -227 | 89 | -1221 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1762 | 1995 | -233 | 88 | 1244 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1762 | 2000 | -238 | 88 | 1238 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1762 | 2000 | -238 | 88 | -1211 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1570 | -205 | 87 | 976 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1362 | 1570 | -208 | 87 | 974 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1359 | 1570 | -211 | 87 | 972 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1353 | 1570 | -217 | 86 | 968 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1352 | 1570 | -218 | 86 | 967 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1346 | 1570 | -224 | 86 | 962 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1686 | 1995 | -309 | 84 | 1185 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1321 | 1570 | -249 | 84 | 944 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1678 | 1995 | -317 | 84 | 1181 | AC

## 1230
Detailed results
Generated at: | 10/07/2026 22:33:54
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3949
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1968 | 1995 | -27 | 99 | 1391 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1942 | 1995 | -53 | 97 | 1372 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1936 | 1995 | -59 | 97 | 1361 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1931 | 1995 | -64 | 97 | 1360 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1929 | 1995 | -66 | 97 | 1366 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1917 | 1995 | -78 | 96 | 1352 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1917 | 1995 | -78 | 96 | 1356 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1908 | 1995 | -87 | 96 | 1344 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1884 | 1995 | -111 | 94 | 1332 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1877 | 2000 | -123 | 94 | 1317 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1877 | 2000 | -123 | 94 | -1291 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1867 | 1995 | -128 | 94 | 1319 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1866 | 2000 | -134 | 93 | -1280 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1866 | 2000 | -134 | 93 | 1311 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1840 | 1995 | -155 | 92 | 1301 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1831 | 1995 | -164 | 92 | 1293 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1805 | 1995 | -190 | 90 | 1274 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1772 | 1995 | -223 | 89 | 1250 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1337 | 1570 | -233 | 85 | 957 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1337 | 1570 | -233 | 85 | 957 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1686 | 1995 | -309 | 85 | 1183 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1678 | 1995 | -317 | 84 | 1179 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1298 | 1570 | -272 | 83 | 928 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1298 | 1570 | -272 | 83 | 928 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1266 | 1570 | -304 | 81 | 906 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1255 | 1570 | -315 | 80 | 898 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1233 | 1570 | -337 | 79 | 883 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1232 | 1570 | -338 | 78 | 881 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1226 | 1570 | -344 | 78 | 878 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1224 | 1570 | -346 | 78 | 876 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1219 | 1570 | -351 | 78 | 872 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1217 | 1570 | -353 | 78 | 871 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1198 | 1570 | -372 | 76 | 857 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1190 | 1570 | -380 | 76 | 851 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1354 | 1890 | -536 | 72 | -943 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1354 | 1890 | -536 | 72 | -943 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1354 | 1920 | -566 | 71 | 964 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1354 | 1920 | -566 | 71 | 964 | AC

## 1330
Detailed results
Generated at: | 10/07/2026 22:33:54
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3931
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1940 | 1995 | -55 | 97 | 1371 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1924 | 1995 | -71 | 96 | 1352 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1918 | 1995 | -77 | 96 | 1349 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1916 | 1995 | -79 | 96 | 1356 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1915 | 1995 | -80 | 96 | 1351 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1902 | 1995 | -93 | 95 | 1345 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1894 | 1995 | -101 | 95 | 1335 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1889 | 1995 | -106 | 95 | 1330 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1887 | 2000 | -113 | 94 | -1297 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1887 | 2000 | -113 | 94 | 1324 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1876 | 2000 | -124 | 94 | 1317 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1876 | 2000 | -124 | 94 | -1286 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1864 | 1995 | -131 | 93 | 1317 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1848 | 1995 | -147 | 93 | 1304 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1826 | 1995 | -169 | 92 | 1289 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1816 | 1995 | -179 | 91 | 1282 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1794 | 1995 | -201 | 90 | 1266 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1762 | 1995 | -233 | 88 | 1242 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1325 | 1570 | -245 | 84 | 946 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1325 | 1570 | -245 | 84 | 946 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1666 | 1995 | -329 | 84 | 1168 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1657 | 1995 | -338 | 83 | 1164 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1284 | 1570 | -286 | 82 | 916 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1284 | 1570 | -286 | 82 | 916 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1249 | 1570 | -321 | 80 | 891 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1242 | 1570 | -328 | 79 | 886 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1223 | 1570 | -347 | 78 | 872 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1219 | 1570 | -351 | 78 | 869 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1213 | 1570 | -357 | 77 | 865 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1211 | 1570 | -359 | 77 | 864 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1207 | 1570 | -363 | 77 | 860 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1201 | 1570 | -369 | 77 | 856 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1184 | 1570 | -386 | 75 | 844 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1177 | 1570 | -393 | 75 | 839 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1349 | 1890 | -541 | 71 | -940 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1349 | 1890 | -541 | 71 | -940 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1349 | 1920 | -571 | 70 | 960 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1349 | 1920 | -571 | 70 | 960 | AC

## 1430
Detailed results
Generated at: | 10/07/2026 22:33:54
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3906
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1917 | 1995 | -78 | 96 | 1355 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1906 | 1995 | -89 | 96 | 1339 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1899 | 1995 | -96 | 95 | 1336 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1899 | 1995 | -96 | 95 | 1344 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1895 | 1995 | -100 | 95 | 1337 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1883 | 1995 | -112 | 94 | 1331 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1880 | 1995 | -115 | 94 | 1325 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1879 | 1995 | -116 | 94 | 1323 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1873 | 2000 | -127 | 94 | 1314 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1873 | 2000 | -127 | 94 | -1287 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1861 | 2000 | -139 | 93 | -1276 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1861 | 2000 | -139 | 93 | 1307 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1847 | 1995 | -148 | 93 | 1304 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1831 | 1995 | -164 | 92 | 1292 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1807 | 1995 | -188 | 91 | 1277 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1802 | 1995 | -193 | 90 | 1271 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1783 | 1995 | -212 | 89 | 1258 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1752 | 1995 | -243 | 88 | 1235 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1335 | 1570 | -235 | 85 | 952 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1335 | 1570 | -235 | 85 | 952 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1650 | 1995 | -345 | 83 | 1157 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1297 | 1570 | -273 | 83 | 926 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1297 | 1570 | -273 | 83 | 926 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1642 | 1995 | -353 | 82 | 1152 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1262 | 1570 | -308 | 80 | 900 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1254 | 1570 | -316 | 80 | 894 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1235 | 1570 | -335 | 79 | 880 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1230 | 1570 | -340 | 78 | 877 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1225 | 1570 | -345 | 78 | 873 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1223 | 1570 | -347 | 78 | 872 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1218 | 1570 | -352 | 78 | 868 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1214 | 1570 | -356 | 77 | 866 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1209 | 1570 | -361 | 77 | 862 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1189 | 1570 | -381 | 76 | 848 | AC

## 1530
Detailed results
Generated at: | 10/07/2026 22:33:54
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3848.65
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1510 | 1570 | -60 | 96 | 1078 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1570 | -92 | 94 | 1054 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1570 | -92 | 94 | 1054 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1570 | -92 | 94 | 1054 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1570 | -92 | 94 | 1054 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1835 | 1995 | -160 | 92 | 1296 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1831 | 1995 | -164 | 92 | 1297 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1570 | -131 | 92 | 1027 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1824 | 1995 | -171 | 91 | 1290 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1823 | 1995 | -172 | 91 | 1289 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1419 | 1570 | -151 | 90 | 1013 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1786 | 1995 | -209 | 90 | 1258 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1400 | 1570 | -170 | 89 | 999 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1400 | 1570 | -170 | 89 | 999 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1778 | 1995 | -217 | 89 | 1262 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1775 | 1995 | -220 | 89 | 1252 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1389 | 1570 | -181 | 88 | 992 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1570 | -182 | 88 | 991 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1762 | 1995 | -233 | 88 | 1248 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1760 | 1995 | -235 | 88 | 1246 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1384 | 1570 | -186 | 88 | 989 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1377 | 1570 | -193 | 88 | 984 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1746 | 1995 | -249 | 88 | 1235 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1723 | 1995 | -272 | 86 | 1219 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1711 | 1995 | -284 | 86 | 1211 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1345 | 1570 | -225 | 86 | 960 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1704 | 1995 | -291 | 85 | 1207 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1694 | 1995 | -301 | 85 | 1198 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1682 | 2000 | -318 | 84 | -1163 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1682 | 2000 | -318 | 84 | 1184 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1672 | 2000 | -328 | 84 | -1153 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1672 | 2000 | -328 | 84 | 1178 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1582 | 1995 | -413 | 79 | 1113 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1574 | 1995 | -421 | 79 | 1109 | AC

## 1630
Detailed results
Generated at: | 10/07/2026 22:33:54
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3710.87
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1527 | 1570 | -43 | 97 | 1088 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1480 | 1570 | -90 | 94 | 1053 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1480 | 1570 | -90 | 94 | 1053 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1474 | 1570 | -96 | 94 | 1050 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1474 | 1570 | -96 | 94 | 1050 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1441 | 1570 | -129 | 92 | 1026 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1417 | 1570 | -153 | 90 | 1010 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1399 | 1570 | -171 | 89 | 997 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1398 | 1570 | -172 | 89 | 997 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1776 | 1995 | -219 | 89 | 1252 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1769 | 1995 | -226 | 89 | 1251 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1390 | 1570 | -180 | 89 | 991 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1389 | 1570 | -181 | 88 | 990 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1764 | 1995 | -231 | 88 | 1245 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1760 | 1995 | -235 | 88 | 1243 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1377 | 1570 | -193 | 88 | 982 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1376 | 1570 | -194 | 88 | 982 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1721 | 1995 | -274 | 86 | 1210 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1713 | 1995 | -282 | 86 | 1214 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1709 | 1995 | -286 | 86 | 1203 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1343 | 1570 | -227 | 86 | 958 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1701 | 1995 | -294 | 85 | 1202 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1698 | 1995 | -297 | 85 | 1201 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1687 | 1995 | -308 | 85 | 1191 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1669 | 1995 | -326 | 84 | 1179 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1664 | 1995 | -331 | 83 | 1176 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1648 | 1995 | -347 | 83 | 1164 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1644 | 1995 | -351 | 82 | 1162 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1609 | 2000 | -391 | 80 | 1133 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1609 | 2000 | -391 | 80 | -1113 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1600 | 2000 | -400 | 80 | -1104 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1600 | 2000 | -400 | 80 | 1127 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1528 | 1995 | -467 | 77 | 1074 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1521 | 1995 | -474 | 76 | 1070 | AC

## 1730
Detailed results
Generated at: | 10/07/2026 22:33:54
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3627.57
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1570 | -131 | 92 | 1027 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1570 | -144 | 91 | 1018 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1570 | -144 | 91 | 1018 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1411 | 1570 | -159 | 90 | 1007 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1411 | 1570 | -159 | 90 | 1007 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1384 | 1570 | -186 | 88 | 988 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1735 | 1995 | -260 | 87 | 1221 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1570 | -209 | 87 | 971 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1729 | 1995 | -266 | 87 | 1221 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1724 | 1995 | -271 | 86 | 1215 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1354 | 1570 | -216 | 86 | 966 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1715 | 1995 | -280 | 86 | 1209 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1348 | 1570 | -222 | 86 | 962 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1341 | 1570 | -229 | 85 | 957 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1336 | 1570 | -234 | 85 | 954 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1324 | 1570 | -246 | 84 | 945 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1682 | 1995 | -313 | 84 | 1180 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1323 | 1570 | -247 | 84 | 944 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1672 | 1995 | -323 | 84 | 1184 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1669 | 1995 | -326 | 84 | 1174 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1663 | 1995 | -332 | 83 | 1174 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1657 | 1995 | -338 | 83 | 1170 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1647 | 1995 | -348 | 83 | 1162 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1290 | 1570 | -280 | 82 | 921 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1633 | 1995 | -362 | 82 | 1152 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1633 | 1995 | -362 | 82 | 1152 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1614 | 1995 | -381 | 81 | 1139 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1605 | 1995 | -390 | 80 | 1133 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1569 | 2000 | -431 | 78 | -1085 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1569 | 2000 | -431 | 78 | 1103 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1559 | 2000 | -441 | 78 | 1098 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1559 | 2000 | -441 | 78 | -1076 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1492 | 1995 | -503 | 75 | 1047 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1485 | 1995 | -510 | 74 | 1044 | AC

## 1830
Detailed results
Generated at: | 10/07/2026 22:33:54
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3590.46
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1394 | 1570 | -176 | 89 | 992 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1394 | 1570 | -176 | 89 | 991 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1394 | 1570 | -176 | 89 | 991 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1368 | 1570 | -202 | 87 | 973 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1368 | 1570 | -202 | 87 | 973 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1736 | 1995 | -259 | 87 | 1222 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1725 | 1995 | -270 | 86 | 1218 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1725 | 1995 | -270 | 86 | 1215 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1352 | 1570 | -218 | 86 | 961 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1711 | 1995 | -284 | 86 | 1206 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1329 | 1570 | -241 | 85 | 944 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1681 | 1995 | -314 | 84 | 1180 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1322 | 1570 | -248 | 84 | 940 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1672 | 1995 | -323 | 84 | 1184 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1314 | 1570 | -256 | 84 | 934 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1668 | 1995 | -327 | 84 | 1172 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1312 | 1570 | -258 | 84 | 932 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1661 | 1995 | -334 | 83 | 1172 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1304 | 1570 | -266 | 83 | 926 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1654 | 1995 | -341 | 83 | 1168 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1646 | 1995 | -349 | 82 | 1161 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1293 | 1570 | -277 | 82 | 918 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1291 | 1570 | -279 | 82 | 917 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1631 | 1995 | -364 | 82 | 1151 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1630 | 1995 | -365 | 82 | 1149 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1608 | 1995 | -387 | 81 | 1134 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1606 | 1995 | -389 | 80 | 1133 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1260 | 1570 | -310 | 80 | 895 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1565 | 2000 | -435 | 78 | 1101 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1565 | 2000 | -435 | 78 | -1083 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1555 | 2000 | -445 | 78 | -1074 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1555 | 2000 | -445 | 78 | 1095 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1485 | 1995 | -510 | 74 | 1042 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1478 | 1995 | -517 | 74 | 1038 | AC

## 1930
Detailed results
Generated at: | 10/07/2026 22:33:54
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3365.62
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1561 | 1570 | -9 | 99 | 1112 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1491 | 1570 | -79 | 95 | 1062 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1491 | 1570 | -79 | 95 | 1062 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1570 | -94 | 94 | 1051 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1474 | 1570 | -96 | 94 | 1049 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1474 | 1570 | -96 | 94 | 1049 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1444 | 1570 | -126 | 92 | 1028 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1570 | -131 | 92 | 1025 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1570 | -144 | 91 | 1015 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1424 | 1570 | -146 | 91 | 1014 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1416 | 1570 | -154 | 90 | 1008 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1570 | -166 | 89 | 1000 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1400 | 1570 | -170 | 89 | 997 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1377 | 1570 | -193 | 88 | 981 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1693 | 1995 | -302 | 85 | 1185 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1673 | 1995 | -322 | 84 | 1172 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1658 | 1995 | -337 | 83 | 1162 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1656 | 1995 | -339 | 83 | 1164 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1581 | 1995 | -414 | 79 | 1109 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1567 | 1995 | -428 | 79 | 1099 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1564 | 1995 | -431 | 78 | 1090 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1558 | 1995 | -437 | 78 | 1094 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1552 | 1995 | -443 | 78 | 1089 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1552 | 1995 | -443 | 78 | 1092 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1547 | 1995 | -448 | 78 | 1080 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1544 | 1995 | -451 | 77 | 1083 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1536 | 1995 | -459 | 77 | 1078 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1512 | 1995 | -483 | 76 | 1060 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1424 | 1995 | -571 | 71 | 997 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1418 | 1995 | -577 | 71 | 993 | AC

## 2030
Detailed results
Generated at: | 10/07/2026 22:33:54
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3137.2
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1572 | 1570 | 2 | 100 | 1120 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1479 | 1570 | -91 | 94 | 1053 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1479 | 1570 | -91 | 94 | 1053 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1570 | -104 | 93 | 1044 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1570 | -127 | 92 | 1028 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1570 | -127 | 92 | 1028 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1433 | 1570 | -137 | 91 | 1020 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1429 | 1570 | -141 | 91 | 1017 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1413 | 1570 | -157 | 90 | 1006 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1411 | 1570 | -159 | 90 | 1005 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1408 | 1570 | -162 | 90 | 1002 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1570 | -182 | 88 | 988 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1386 | 1570 | -184 | 88 | 987 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1370 | 1570 | -200 | 87 | 975 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1642 | 1995 | -353 | 82 | 1145 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1622 | 1995 | -373 | 81 | 1133 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1607 | 1995 | -388 | 81 | 1123 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1602 | 1995 | -393 | 80 | 1123 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1522 | 1995 | -473 | 76 | 1064 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1509 | 1995 | -486 | 76 | 1054 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1507 | 1995 | -488 | 76 | 1056 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1496 | 1995 | -499 | 75 | 1046 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1495 | 1995 | -500 | 75 | 1036 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1491 | 1995 | -504 | 75 | 1044 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1481 | 1995 | -514 | 74 | 1038 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1475 | 1995 | -520 | 74 | 1025 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1465 | 1995 | -530 | 73 | 1024 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1451 | 1995 | -544 | 73 | 1013 | AC

## 2130
Detailed results
Generated at: | 10/07/2026 22:33:54
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3201.31
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1573 | 1570 | 3 | 100 | 1120 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1570 | -94 | 94 | 1051 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1570 | -94 | 94 | 1051 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1469 | 1570 | -101 | 94 | 1044 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1570 | -127 | 92 | 1028 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1570 | -127 | 92 | 1028 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1437 | 1570 | -133 | 92 | 1024 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1430 | 1570 | -140 | 91 | 1018 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1411 | 1570 | -159 | 90 | 1006 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1410 | 1570 | -160 | 90 | 1005 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1408 | 1570 | -162 | 90 | 1003 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1383 | 1570 | -187 | 88 | 986 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1381 | 1570 | -189 | 88 | 985 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1570 | -209 | 87 | 971 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1691 | 1995 | -304 | 85 | 1182 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1663 | 1995 | -332 | 83 | 1163 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1640 | 1995 | -355 | 82 | 1147 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1626 | 1995 | -369 | 82 | 1142 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1559 | 1995 | -436 | 78 | 1092 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1546 | 1995 | -449 | 77 | 1082 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1542 | 1995 | -452 | 77 | 1082 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1536 | 1995 | -459 | 77 | 1067 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1533 | 1995 | -462 | 77 | 1074 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1529 | 1995 | -466 | 77 | 1072 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1523 | 1995 | -472 | 76 | 1070 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1514 | 1995 | -481 | 76 | 1054 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1503 | 1995 | -492 | 75 | 1053 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1485 | 1995 | -510 | 74 | 1038 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1405 | 1995 | -590 | 70 | 982 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1400 | 1995 | -595 | 70 | 979 | AC

## 2230
Detailed results
Generated at: | 10/07/2026 22:33:54
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3442.04
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1574 | 1570 | 4 | 100 | 1120 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1570 | -76 | 95 | 1063 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1570 | -76 | 95 | 1063 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1570 | -92 | 94 | 1051 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1474 | 1570 | -96 | 94 | 1050 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1474 | 1570 | -96 | 94 | 1050 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1452 | 1570 | -118 | 92 | 1035 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1447 | 1570 | -123 | 92 | 1030 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1430 | 1570 | -140 | 91 | 1019 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1428 | 1570 | -142 | 91 | 1018 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1419 | 1570 | -151 | 90 | 1011 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1403 | 1570 | -167 | 89 | 1000 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1399 | 1570 | -171 | 89 | 998 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1760 | 1995 | -235 | 88 | 1231 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1376 | 1570 | -194 | 88 | 982 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1729 | 1995 | -266 | 87 | 1210 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1706 | 1995 | -289 | 86 | 1194 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1685 | 1995 | -310 | 84 | 1182 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1632 | 1995 | -363 | 82 | 1143 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1627 | 1995 | -368 | 82 | 1131 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1619 | 1995 | -376 | 81 | 1133 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1615 | 1995 | -380 | 81 | 1134 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1609 | 1995 | -386 | 81 | 1128 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1606 | 1995 | -389 | 81 | 1119 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1604 | 1995 | -391 | 80 | 1124 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1596 | 1995 | -399 | 80 | 1119 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1593 | 1995 | -402 | 80 | 1117 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1564 | 1995 | -431 | 78 | 1094 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1465 | 1995 | -530 | 73 | 1023 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1458 | 1995 | -537 | 73 | 1020 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1454 | 2000 | -546 | 73 | 1014 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1454 | 2000 | -546 | 73 | -998 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1443 | 2000 | -557 | 72 | -991 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1443 | 2000 | -557 | 72 | 1009 | AC

## 2330
Detailed results
Generated at: | 10/07/2026 22:33:55
Business day: | 2026-07-12
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3883
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00105 | RO | RROVI31 _generator | 0 | 310 |  |  | 310 | 1 |  | 310 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 306 |  | 389 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 26 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 58 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 1 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 9 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 340 | 259 |  | 340 | 0 | FALSE | FALSE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 118 | 0 |  | 118 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 14 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 22 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 29 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 23 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 23 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 21 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 24 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 9 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 11 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 17 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 0 | 32 |  | 32 | 0 | TRUE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 22 | 67 |  | 67 | 0 | FALSE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 9 |  | 9 | 0 | FALSE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 3 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 3 | 24 |  | 24 | 0 | FALSE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 13 |  | 13 | 0 | FALSE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 10 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 31 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 44 |  | 44 | 0 | FALSE | FALSE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 11 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 9 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 1 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 0 | 96 |  | 96 | 0 | TRUE | FALSE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 0 | 58 |  | 58 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1989 | 1995 | -6 | 100 | 1398 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1949 | 2000 | -51 | 97 | -1337 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1949 | 2000 | -51 | 97 | 1366 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1940 | 1995 | -55 | 97 | 1365 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1936 | 2000 | -64 | 97 | -1325 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1936 | 2000 | -64 | 97 | 1358 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1922 | 1995 | -73 | 96 | 1348 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1916 | 1995 | -79 | 96 | 1355 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1904 | 1995 | -91 | 95 | 1338 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1887 | 1995 | -108 | 95 | 1332 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1870 | 1995 | -125 | 94 | 1319 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1869 | 1995 | -126 | 94 | 1314 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1851 | 1995 | -144 | 93 | 1304 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1849 | 1995 | -146 | 93 | 1303 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1849 | 1995 | -146 | 93 | 1302 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1848 | 1995 | -147 | 93 | 1301 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1842 | 1995 | -153 | 92 | 1298 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1806 | 1995 | -189 | 91 | 1272 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1395 | 1570 | -175 | 89 | 992 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1570 | -178 | 89 | 990 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1570 | -178 | 89 | 990 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1372 | 1570 | -198 | 87 | 974 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1372 | 1570 | -198 | 87 | 974 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1359 | 1570 | -211 | 87 | 966 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1320 | 1570 | -250 | 84 | 939 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1318 | 1570 | -252 | 84 | 937 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1317 | 1570 | -253 | 84 | 937 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1656 | 1995 | -339 | 83 | 1155 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1301 | 1570 | -269 | 83 | 925 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1297 | 1570 | -273 | 83 | 921 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1647 | 1995 | -348 | 83 | 1150 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1295 | 1570 | -275 | 82 | 921 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1293 | 1570 | -277 | 82 | 920 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1254 | 1570 | -316 | 80 | 891 | AC