## 0030Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3073
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1465 | 1570 | 1570 | -105 | 93 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1463 | 1570 | 1570 | -107 | 93 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1463 | 1570 | 1570 | -107 | 93 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1460 | 1570 | 1570 | -110 | 93 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 | 1570 | 1570 | -126 | 92 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1417 | 1570 | 1570 | -153 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 | 1570 | 1570 | -155 | 90 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 | 1570 | 1570 | -155 | 90 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1414 | 1570 | 1570 | -156 | 90 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1395 | 1570 | 1570 | -175 | 89 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1395 | 1570 | 1570 | -175 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1393 | 1570 | 1570 | -177 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1390 | 1570 | 1570 | -180 | 89 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1648 | 1995 | 1995 | -347 | 83 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1630 | 1995 | 1995 | -365 | 82 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1625 | 1995 | 1995 | -370 | 81 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1017 | -1248 | -1248 | -232 | 81 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1015 | -1248 | -1248 | -234 | 81 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1619 | 1995 | 1995 | -376 | 81 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1008 | -1248 | -1248 | -240 | 81 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1606 | 1995 | 1995 | -389 | 80 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1584 | 1995 | 1995 | -411 | 79 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1582 | 1995 | 1995 | -413 | 79 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1575 | 1995 | 1995 | -420 | 79 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1574 | 1995 | 1995 | -421 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1561 | 1995 | 1995 | -434 | 78 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1560 | 1995 | 1995 | -435 | 78 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1550 | 1995 | 1995 | -445 | 78 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1532 | 1995 | 1995 | -463 | 77 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1524 | 1995 | 1995 | -471 | 76 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1498 | 2000 | 2000 | -502 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1494 | -2000 | -2000 | -506 | 75 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1485 | 2000 | 2000 | -515 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1481 | -2000 | -2000 | -519 | 74 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 | 1995 | 1995 | -579 | 71 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1399 | 1995 | 1995 | -596 | 70 | []

## 0030Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3073
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1465 |  | 1570 | -105 | 93 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1463 |  | 1570 | -107 | 93 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1463 |  | 1570 | -107 | 93 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1460 |  | 1570 | -110 | 93 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 |  | 1570 | -126 | 92 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1417 |  | 1570 | -153 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 |  | 1570 | -155 | 90 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 |  | 1570 | -155 | 90 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1414 |  | 1570 | -156 | 90 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1395 |  | 1570 | -175 | 89 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1395 |  | 1570 | -175 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1393 |  | 1570 | -177 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1390 |  | 1570 | -180 | 89 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1648 |  | 1995 | -347 | 83 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1630 |  | 1995 | -365 | 82 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1625 |  | 1995 | -370 | 81 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1017 |  | -1248 | -232 | 81 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1015 |  | -1248 | -234 | 81 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1619 |  | 1995 | -376 | 81 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1008 |  | -1248 | -240 | 81 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1606 |  | 1995 | -389 | 80 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1584 |  | 1995 | -411 | 79 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1582 |  | 1995 | -413 | 79 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1575 |  | 1995 | -420 | 79 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1574 |  | 1995 | -421 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1561 |  | 1995 | -434 | 78 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1560 |  | 1995 | -435 | 78 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1550 |  | 1995 | -445 | 78 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1532 |  | 1995 | -463 | 77 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1524 |  | 1995 | -471 | 76 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1498 |  | 2000 | -502 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1494 |  | -2000 | -506 | 75 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1485 |  | 2000 | -515 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1481 |  | -2000 | -519 | 74 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 |  | 1995 | -579 | 71 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1399 |  | 1995 | -596 | 70 | []

## 0130Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3196
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1569 | 1570 | 1570 | -1 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1489 | 1570 | 1570 | -81 | 95 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1489 | 1570 | 1570 | -81 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1481 | 1570 | 1570 | -89 | 94 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1474 | 1570 | 1570 | -96 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1460 | 1570 | 1570 | -110 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1434 | 1570 | 1570 | -136 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1434 | 1570 | 1570 | -136 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1434 | 1570 | 1570 | -136 | 91 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 | 1570 | 1570 | -137 | 91 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 | 1570 | 1570 | -155 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1412 | 1570 | 1570 | -158 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1411 | 1570 | 1570 | -159 | 90 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1408 | 1570 | 1570 | -162 | 90 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1678 | 1995 | 1995 | -317 | 84 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1674 | 1995 | 1995 | -321 | 84 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1664 | 1995 | 1995 | -331 | 83 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1039 | -1248 | -1248 | -209 | 83 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1037 | -1248 | -1248 | -211 | 83 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1654 | 1995 | 1995 | -341 | 83 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1650 | 1995 | 1995 | -345 | 83 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1031 | -1248 | -1248 | -218 | 83 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1024 | -1248 | -1248 | -225 | 82 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1628 | 1995 | 1995 | -367 | 82 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1625 | 1995 | 1995 | -370 | 81 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1616 | 1995 | 1995 | -379 | 81 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1613 | 1995 | 1995 | -382 | 81 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1598 | 1995 | 1995 | -397 | 80 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1596 | 1995 | 1995 | -399 | 80 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1587 | 1995 | 1995 | -408 | 80 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1568 | 1995 | 1995 | -427 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1562 | 1995 | 1995 | -433 | 78 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1561 | 2000 | 2000 | -439 | 78 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1557 | -2000 | -2000 | -443 | 78 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1546 | 2000 | 2000 | -454 | 77 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1543 | -2000 | -2000 | -457 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1448 | 1995 | 1995 | -547 | 73 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1430 | 1995 | 1995 | -565 | 72 | []

## 0130Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3196
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1570 | -1 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1489 |  | 1570 | -81 | 95 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1489 |  | 1570 | -81 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1481 |  | 1570 | -89 | 94 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1474 |  | 1570 | -96 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1460 |  | 1570 | -110 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1434 |  | 1570 | -136 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1434 |  | 1570 | -136 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1434 |  | 1570 | -136 | 91 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 |  | 1570 | -137 | 91 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 |  | 1570 | -155 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1412 |  | 1570 | -158 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1411 |  | 1570 | -159 | 90 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1408 |  | 1570 | -162 | 90 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1678 |  | 1995 | -317 | 84 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1674 |  | 1995 | -321 | 84 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1664 |  | 1995 | -331 | 83 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1039 |  | -1248 | -209 | 83 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1037 |  | -1248 | -211 | 83 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1654 |  | 1995 | -341 | 83 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1650 |  | 1995 | -345 | 83 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1031 |  | -1248 | -218 | 83 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1024 |  | -1248 | -225 | 82 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1628 |  | 1995 | -367 | 82 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1625 |  | 1995 | -370 | 81 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1616 |  | 1995 | -379 | 81 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1613 |  | 1995 | -382 | 81 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1598 |  | 1995 | -397 | 80 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1596 |  | 1995 | -399 | 80 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1587 |  | 1995 | -408 | 80 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1568 |  | 1995 | -427 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1562 |  | 1995 | -433 | 78 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1561 |  | 2000 | -439 | 78 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1557 |  | -2000 | -443 | 78 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1546 |  | 2000 | -454 | 77 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1543 |  | -2000 | -457 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1448 |  | 1995 | -547 | 73 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1430 |  | 1995 | -565 | 72 | []

## 0230Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3364
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 | 1570 | 1570 | -3 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1509 | 1570 | 1570 | -61 | 96 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1509 | 1570 | 1570 | -61 | 96 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1483 | 1570 | 1570 | -87 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1481 | 1570 | 1570 | -89 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1467 | 1570 | 1570 | -103 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1447 | 1570 | 1570 | -123 | 92 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1446 | 1570 | 1570 | -124 | 92 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 | 1570 | 1570 | -126 | 92 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1443 | 1570 | 1570 | -127 | 92 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 | 1570 | 1570 | -143 | 91 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1422 | 1570 | 1570 | -148 | 91 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1419 | 1570 | 1570 | -151 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1414 | 1570 | 1570 | -156 | 90 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1704 | 1995 | 1995 | -291 | 85 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1696 | 1995 | 1995 | -299 | 85 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1061 | -1248 | -1248 | -188 | 85 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1059 | -1248 | -1248 | -190 | 85 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1690 | 1995 | 1995 | -305 | 85 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1688 | 1995 | 1995 | -307 | 85 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1052 | -1248 | -1248 | -196 | 84 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1676 | 1995 | 1995 | -319 | 84 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1670 | 1995 | 1995 | -325 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1045 | -1248 | -1248 | -204 | 84 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1669 | 1995 | 1995 | -326 | 84 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1658 | 1995 | 1995 | -337 | 83 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1658 | 2000 | 2000 | -342 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1656 | -2000 | -2000 | -344 | 83 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1642 | 1995 | 1995 | -353 | 82 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1643 | 2000 | 2000 | -357 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1641 | -2000 | -2000 | -359 | 82 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1630 | 1995 | 1995 | -365 | 82 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1628 | 1995 | 1995 | -367 | 82 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1619 | 1995 | 1995 | -376 | 81 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1601 | 1995 | 1995 | -394 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1598 | 1995 | 1995 | -397 | 80 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1469 | 1995 | 1995 | -526 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1449 | 1995 | 1995 | -546 | 73 | []

## 0230Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3364
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 |  | 1570 | -3 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1509 |  | 1570 | -61 | 96 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1509 |  | 1570 | -61 | 96 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1483 |  | 1570 | -87 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1481 |  | 1570 | -89 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1467 |  | 1570 | -103 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1447 |  | 1570 | -123 | 92 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1446 |  | 1570 | -124 | 92 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 |  | 1570 | -126 | 92 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1443 |  | 1570 | -127 | 92 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1570 | -143 | 91 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1422 |  | 1570 | -148 | 91 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1419 |  | 1570 | -151 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1414 |  | 1570 | -156 | 90 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1704 |  | 1995 | -291 | 85 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1696 |  | 1995 | -299 | 85 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1061 |  | -1248 | -188 | 85 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1059 |  | -1248 | -190 | 85 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1690 |  | 1995 | -305 | 85 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1688 |  | 1995 | -307 | 85 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1052 |  | -1248 | -196 | 84 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1676 |  | 1995 | -319 | 84 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1670 |  | 1995 | -325 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1045 |  | -1248 | -204 | 84 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1669 |  | 1995 | -326 | 84 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1658 |  | 1995 | -337 | 83 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1658 |  | 2000 | -342 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1656 |  | -2000 | -344 | 83 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1642 |  | 1995 | -353 | 82 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1643 |  | 2000 | -357 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1641 |  | -2000 | -359 | 82 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1630 |  | 1995 | -365 | 82 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1628 |  | 1995 | -367 | 82 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1619 |  | 1995 | -376 | 81 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1601 |  | 1995 | -394 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1598 |  | 1995 | -397 | 80 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1469 |  | 1995 | -526 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1449 |  | 1995 | -546 | 73 | []

## 0330Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3206
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 | 1570 | 1570 | -3 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1490 | 1570 | 1570 | -80 | 95 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1490 | 1570 | 1570 | -80 | 95 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1480 | 1570 | 1570 | -90 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1471 | 1570 | 1570 | -99 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1457 | 1570 | 1570 | -113 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 | 1570 | 1570 | -134 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 | 1570 | 1570 | -135 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 | 1570 | 1570 | -137 | 91 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 | 1570 | 1570 | -137 | 91 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1417 | 1570 | 1570 | -153 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1413 | 1570 | 1570 | -157 | 90 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1410 | 1570 | 1570 | -160 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1404 | 1570 | 1570 | -166 | 89 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1045 | -1248 | -1248 | -203 | 84 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1043 | -1248 | -1248 | -205 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1037 | -1248 | -1248 | -212 | 83 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1651 | 1995 | 1995 | -344 | 83 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1632 | 1995 | 1995 | -363 | 82 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1630 | 1995 | 1995 | -365 | 82 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1627 | 1995 | 1995 | -368 | 82 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1611 | 1995 | 1995 | -384 | 81 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1611 | 1995 | 1995 | -384 | 81 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1602 | 1995 | 1995 | -393 | 80 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1591 | 1995 | 1995 | -404 | 80 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1586 | 2000 | 2000 | -414 | 79 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1581 | 1995 | 1995 | -414 | 79 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1581 | 1995 | 1995 | -414 | 79 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1583 | -2000 | -2000 | -417 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1568 | 1995 | 1995 | -427 | 79 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1571 | 2000 | 2000 | -429 | 79 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1569 | -2000 | -2000 | -431 | 78 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1564 | 1995 | 1995 | -431 | 78 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1551 | 1995 | 1995 | -444 | 78 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1538 | 1995 | 1995 | -457 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1415 | 1995 | 1995 | -580 | 71 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1397 | 1995 | 1995 | -598 | 70 | []

## 0330Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3206
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 |  | 1570 | -3 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1490 |  | 1570 | -80 | 95 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1490 |  | 1570 | -80 | 95 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1480 |  | 1570 | -90 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1471 |  | 1570 | -99 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1457 |  | 1570 | -113 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 |  | 1570 | -134 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1570 | -135 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 |  | 1570 | -137 | 91 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 |  | 1570 | -137 | 91 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1417 |  | 1570 | -153 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1413 |  | 1570 | -157 | 90 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1410 |  | 1570 | -160 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1404 |  | 1570 | -166 | 89 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1045 |  | -1248 | -203 | 84 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1043 |  | -1248 | -205 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1037 |  | -1248 | -212 | 83 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1651 |  | 1995 | -344 | 83 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1632 |  | 1995 | -363 | 82 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1630 |  | 1995 | -365 | 82 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1627 |  | 1995 | -368 | 82 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1611 |  | 1995 | -384 | 81 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1611 |  | 1995 | -384 | 81 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1602 |  | 1995 | -393 | 80 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1591 |  | 1995 | -404 | 80 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1586 |  | 2000 | -414 | 79 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1581 |  | 1995 | -414 | 79 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1581 |  | 1995 | -414 | 79 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1583 |  | -2000 | -417 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1568 |  | 1995 | -427 | 79 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1571 |  | 2000 | -429 | 79 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1569 |  | -2000 | -431 | 78 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1564 |  | 1995 | -431 | 78 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1551 |  | 1995 | -444 | 78 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1538 |  | 1995 | -457 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1415 |  | 1995 | -580 | 71 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1397 |  | 1995 | -598 | 70 | []

## 0430Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3201
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 | 1570 | 1570 | -3 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 | 1570 | 1570 | -85 | 95 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 | 1570 | 1570 | -85 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1474 | 1570 | 1570 | -96 | 94 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1468 | 1570 | 1570 | -102 | 93 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1455 | 1570 | 1570 | -115 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1430 | 1570 | 1570 | -140 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1429 | 1570 | 1570 | -141 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1428 | 1570 | 1570 | -142 | 91 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 | 1570 | 1570 | -143 | 91 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1411 | 1570 | 1570 | -159 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1408 | 1570 | 1570 | -162 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 | 1570 | 1570 | -165 | 90 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 | 1570 | 1570 | -165 | 90 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1683 | 1995 | 1995 | -312 | 84 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1663 | 1995 | 1995 | -332 | 83 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1656 | 1995 | 1995 | -339 | 83 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1035 | -1248 | -1248 | -213 | 83 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1033 | -1248 | -1248 | -215 | 83 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1650 | 1995 | 1995 | -345 | 83 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1643 | 1995 | 1995 | -352 | 82 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1026 | -1248 | -1248 | -222 | 82 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1630 | 1995 | 1995 | -365 | 82 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1019 | -1248 | -1248 | -229 | 82 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1621 | 1995 | 1995 | -374 | 81 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1611 | 1995 | 1995 | -384 | 81 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1606 | 1995 | 1995 | -389 | 81 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1599 | 1995 | 1995 | -396 | 80 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1593 | 1995 | 1995 | -402 | 80 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1585 | 1995 | 1995 | -410 | 79 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1588 | 2000 | 2000 | -412 | 79 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1585 | -2000 | -2000 | -415 | 79 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1570 | 1995 | 1995 | -425 | 79 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1573 | 2000 | 2000 | -427 | 79 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1571 | -2000 | -2000 | -429 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1558 | 1995 | 1995 | -437 | 78 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1441 | 1995 | 1995 | -554 | 72 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1422 | 1995 | 1995 | -573 | 71 | []

## 0430Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3201
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 |  | 1570 | -3 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 |  | 1570 | -85 | 95 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 |  | 1570 | -85 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1474 |  | 1570 | -96 | 94 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1468 |  | 1570 | -102 | 93 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1455 |  | 1570 | -115 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1430 |  | 1570 | -140 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1429 |  | 1570 | -141 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1428 |  | 1570 | -142 | 91 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1570 | -143 | 91 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1411 |  | 1570 | -159 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1408 |  | 1570 | -162 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 |  | 1570 | -165 | 90 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 |  | 1570 | -165 | 90 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1683 |  | 1995 | -312 | 84 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1663 |  | 1995 | -332 | 83 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1656 |  | 1995 | -339 | 83 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1035 |  | -1248 | -213 | 83 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1033 |  | -1248 | -215 | 83 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1650 |  | 1995 | -345 | 83 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1643 |  | 1995 | -352 | 82 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1026 |  | -1248 | -222 | 82 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1630 |  | 1995 | -365 | 82 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1019 |  | -1248 | -229 | 82 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1621 |  | 1995 | -374 | 81 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1611 |  | 1995 | -384 | 81 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1606 |  | 1995 | -389 | 81 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1599 |  | 1995 | -396 | 80 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1593 |  | 1995 | -402 | 80 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1585 |  | 1995 | -410 | 79 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1588 |  | 2000 | -412 | 79 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1585 |  | -2000 | -415 | 79 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1570 |  | 1995 | -425 | 79 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1573 |  | 2000 | -427 | 79 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1571 |  | -2000 | -429 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1558 |  | 1995 | -437 | 78 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1441 |  | 1995 | -554 | 72 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1422 |  | 1995 | -573 | 71 | []

## 0530Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3125
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1478 | 1570 | 1570 | -92 | 94 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1470 | 1570 | 1570 | -100 | 94 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1470 | 1570 | 1570 | -100 | 94 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 | 1570 | 1570 | -118 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1449 | 1570 | 1570 | -121 | 92 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1419 | 1570 | 1570 | -151 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1418 | 1570 | 1570 | -152 | 90 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1418 | 1570 | 1570 | -152 | 90 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1417 | 1570 | 1570 | -153 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 | 1570 | 1570 | -165 | 90 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1399 | 1570 | 1570 | -171 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1397 | 1570 | 1570 | -173 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1395 | 1570 | 1570 | -175 | 89 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1692 | 1995 | 1995 | -303 | 85 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1678 | 1995 | 1995 | -317 | 84 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1675 | 1995 | 1995 | -320 | 84 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1662 | 1995 | 1995 | -333 | 83 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1642 | 1995 | 1995 | -353 | 82 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1017 | -1248 | -1248 | -232 | 81 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1619 | 1995 | 1995 | -376 | 81 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1010 | -1248 | -1248 | -238 | 81 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1613 | 1995 | 1995 | -382 | 81 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1613 | 1995 | 1995 | -382 | 81 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1604 | 1995 | 1995 | -391 | 80 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1599 | 1995 | 1995 | -396 | 80 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1596 | 1995 | 1995 | -399 | 80 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1586 | 1995 | 1995 | -409 | 80 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1568 | 1995 | 1995 | -427 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1555 | 1995 | 1995 | -440 | 78 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1532 | 2000 | 2000 | -468 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1529 | -2000 | -2000 | -471 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1518 | 2000 | 2000 | -482 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1515 | -2000 | -2000 | -485 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1451 | 1995 | 1995 | -544 | 73 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1433 | 1995 | 1995 | -562 | 72 | []

## 0530Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3125
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1478 |  | 1570 | -92 | 94 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1470 |  | 1570 | -100 | 94 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1470 |  | 1570 | -100 | 94 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1570 | -118 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1449 |  | 1570 | -121 | 92 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1419 |  | 1570 | -151 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1418 |  | 1570 | -152 | 90 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1418 |  | 1570 | -152 | 90 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1417 |  | 1570 | -153 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 |  | 1570 | -165 | 90 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1399 |  | 1570 | -171 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1397 |  | 1570 | -173 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1395 |  | 1570 | -175 | 89 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1692 |  | 1995 | -303 | 85 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1678 |  | 1995 | -317 | 84 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1675 |  | 1995 | -320 | 84 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1662 |  | 1995 | -333 | 83 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1642 |  | 1995 | -353 | 82 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1017 |  | -1248 | -232 | 81 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1619 |  | 1995 | -376 | 81 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1010 |  | -1248 | -238 | 81 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1613 |  | 1995 | -382 | 81 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1613 |  | 1995 | -382 | 81 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1604 |  | 1995 | -391 | 80 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1599 |  | 1995 | -396 | 80 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1596 |  | 1995 | -399 | 80 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1586 |  | 1995 | -409 | 80 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1568 |  | 1995 | -427 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1555 |  | 1995 | -440 | 78 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1532 |  | 2000 | -468 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1529 |  | -2000 | -471 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1518 |  | 2000 | -482 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1515 |  | -2000 | -485 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1451 |  | 1995 | -544 | 73 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1433 |  | 1995 | -562 | 72 | []

## 0630Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2040
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1468 | 1570 | 1570 | -102 | 93 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1446 | 1570 | 1570 | -124 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1440 | 1570 | 1570 | -130 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1401 | 1570 | 1570 | -169 | 89 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1377 | 1570 | 1570 | -193 | 88 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1358 | 1570 | 1570 | -212 | 87 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1358 | 1570 | 1570 | -212 | 86 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1351 | 1570 | 1570 | -219 | 86 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1351 | 1570 | 1570 | -219 | 86 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1336 | 1570 | 1570 | -234 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1332 | 1570 | 1570 | -238 | 85 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1328 | 1570 | 1570 | -242 | 85 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1604 | 1995 | 1995 | -391 | 80 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -911 | -1248 | -1248 | -337 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -910 | -1248 | -1248 | -339 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -346 | 72 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1442 | 1995 | 1995 | -553 | 72 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1440 | 1995 | 1995 | -555 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -896 | -1248 | -1248 | -352 | 72 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 | 1995 | 1995 | -579 | 71 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 | 1995 | 1995 | -579 | 71 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 | 1995 | 1995 | -579 | 71 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 | 1995 | 1995 | -579 | 71 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1405 | 1995 | 1995 | -590 | 70 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1398 | 1995 | 1995 | -597 | 70 | []

## 0630Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2040
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1468 |  | 1570 | -102 | 93 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1446 |  | 1570 | -124 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1440 |  | 1570 | -130 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1401 |  | 1570 | -169 | 89 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1377 |  | 1570 | -193 | 88 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1358 |  | 1570 | -212 | 87 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1358 |  | 1570 | -212 | 86 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1351 |  | 1570 | -219 | 86 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1351 |  | 1570 | -219 | 86 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1336 |  | 1570 | -234 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1332 |  | 1570 | -238 | 85 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1328 |  | 1570 | -242 | 85 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1604 |  | 1995 | -391 | 80 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -911 |  | -1248 | -337 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -910 |  | -1248 | -339 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -346 | 72 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1442 |  | 1995 | -553 | 72 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1440 |  | 1995 | -555 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -896 |  | -1248 | -352 | 72 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 |  | 1995 | -579 | 71 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 |  | 1995 | -579 | 71 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 |  | 1995 | -579 | 71 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 |  | 1995 | -579 | 71 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1405 |  | 1995 | -590 | 70 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1398 |  | 1995 | -597 | 70 | []

## 0730Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 1091
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 | 1570 | 1570 | -101 | 94 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1463 | 1570 | 1570 | -107 | 93 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1385 | 1570 | 1570 | -185 | 88 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 | 1570 | 1570 | -202 | 87 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1307 | 1570 | 1570 | -263 | 83 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1303 | 1570 | 1570 | -267 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1300 | 1570 | 1570 | -270 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1291 | 1570 | 1570 | -279 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1282 | 1570 | 1570 | -288 | 82 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1274 | 1570 | 1570 | -296 | 81 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1251 | 1570 | 1570 | -319 | 80 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1251 | 1570 | 1570 | -319 | 80 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RIS1A41 _XVK_IS11_1:line | -1242 | -1722 | -1722 | -480 | 72 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RIS1A41 _XVK_IS11_1:line | -1222 | -1722 | -1722 | -500 | 71 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1411 | 1995 | 1995 | -584 | 71 | []

## 0730Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 1091
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 |  | 1570 | -101 | 94 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1463 |  | 1570 | -107 | 93 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1385 |  | 1570 | -185 | 88 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 |  | 1570 | -202 | 87 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1307 |  | 1570 | -263 | 83 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1303 |  | 1570 | -267 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1300 |  | 1570 | -270 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1291 |  | 1570 | -279 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1282 |  | 1570 | -288 | 82 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1274 |  | 1570 | -296 | 81 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1251 |  | 1570 | -319 | 80 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1251 |  | 1570 | -319 | 80 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RIS1A41 _XVK_IS11_1:line | -1242 |  | -1722 | -480 | 72 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RIS1A41 _XVK_IS11_1:line | -1222 |  | -1722 | -500 | 71 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1411 |  | 1995 | -584 | 71 | []

## 0830Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 840
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1570 | 1570 | 1570 | 0 | 100 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 | 1570 | 1570 | -85 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1462 | 1570 | 1570 | -108 | 93 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 772 | 870 | 870 | -98 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 767 | 870 | 870 | -103 | 88 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1381 | 1570 | 1570 | -189 | 88 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1360 | 1570 | 1570 | -210 | 87 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1301 | 1570 | 1570 | -269 | 83 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1291 | 1570 | 1570 | -279 | 82 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1289 | 1570 | 1570 | -281 | 82 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1281 | 1570 | 1570 | -289 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1270 | 1570 | 1570 | -300 | 81 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1264 | 1570 | 1570 | -306 | 80 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1118 | 1570 | 1570 | -452 | 71 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RIS1A41 _XVK_IS11_1:line | -1226 | -1722 | -1722 | -496 | 71 | []

## 0830Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 840
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1570 |  | 1570 | 0 | 100 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 |  | 1570 | -85 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1462 |  | 1570 | -108 | 93 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 772 |  | 870 | -98 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 767 |  | 870 | -103 | 88 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1381 |  | 1570 | -189 | 88 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1360 |  | 1570 | -210 | 87 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1301 |  | 1570 | -269 | 83 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1291 |  | 1570 | -279 | 82 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1289 |  | 1570 | -281 | 82 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1281 |  | 1570 | -289 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1270 |  | 1570 | -300 | 81 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1264 |  | 1570 | -306 | 80 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1118 |  | 1570 | -452 | 71 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RIS1A41 _XVK_IS11_1:line | -1226 |  | -1722 | -496 | 71 | []

## 0930Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 1025
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1478 | 1570 | 1570 | -92 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1445 | 1570 | 1570 | -125 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1393 | 1570 | 1570 | -177 | 89 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1377 | 1570 | 1570 | -193 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 754 | 870 | 870 | -116 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 749 | 870 | 870 | -121 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1317 | 1570 | 1570 | -253 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1299 | 1570 | 1570 | -271 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1299 | 1570 | 1570 | -271 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1295 | 1570 | 1570 | -275 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1285 | 1570 | 1570 | -285 | 82 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1276 | 1570 | 1570 | -294 | 81 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1137 | 1570 | 1570 | -433 | 72 | []

## 0930Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 1025
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1478 |  | 1570 | -92 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1445 |  | 1570 | -125 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1393 |  | 1570 | -177 | 89 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1377 |  | 1570 | -193 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 754 |  | 870 | -116 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 749 |  | 870 | -121 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1317 |  | 1570 | -253 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1299 |  | 1570 | -271 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1299 |  | 1570 | -271 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1295 |  | 1570 | -275 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1285 |  | 1570 | -285 | 82 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1276 |  | 1570 | -294 | 81 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1137 |  | 1570 | -433 | 72 | []

## 1030Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 841
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1566 | -1570 | -1570 | -4 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1456 | -1570 | -1570 | -114 | 93 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 793 | 870 | 870 | -77 | 91 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 789 | 870 | 870 | -81 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1415 | -1570 | -1570 | -155 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1341 | -1570 | -1570 | -229 | 85 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1332 | -1570 | -1570 | -238 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1279 | -1570 | -1570 | -291 | 81 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1262 | -1570 | -1570 | -308 | 80 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1261 | -1570 | -1570 | -309 | 80 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1260 | -1570 | -1570 | -310 | 80 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1250 | -1570 | -1570 | -320 | 80 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1241 | -1570 | -1570 | -329 | 79 | []

## 1030Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 841
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1566 |  | -1570 | -4 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1456 |  | -1570 | -114 | 93 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 793 |  | 870 | -77 | 91 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 789 |  | 870 | -81 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1415 |  | -1570 | -155 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1341 |  | -1570 | -229 | 85 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1332 |  | -1570 | -238 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1279 |  | -1570 | -291 | 81 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1262 |  | -1570 | -308 | 80 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1261 |  | -1570 | -309 | 80 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1260 |  | -1570 | -310 | 80 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1250 |  | -1570 | -320 | 80 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1241 |  | -1570 | -329 | 79 | []

## 1130Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 1226
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1570 | 1570 | 1570 | 0 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1488 | 1570 | 1570 | -82 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1464 | 1570 | 1570 | -106 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1412 | 1570 | 1570 | -158 | 90 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1392 | 1570 | 1570 | -178 | 89 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1335 | 1570 | 1570 | -235 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 735 | 870 | 870 | -135 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 731 | 870 | 870 | -139 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1319 | 1570 | 1570 | -251 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1314 | 1570 | 1570 | -256 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1303 | 1570 | 1570 | -267 | 83 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1300 | 1570 | 1570 | -270 | 83 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1293 | 1570 | 1570 | -277 | 82 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1208 | 1570 | 1570 | -362 | 77 | []

## 1130Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 1226
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1570 |  | 1570 | 0 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1488 |  | 1570 | -82 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1464 |  | 1570 | -106 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1412 |  | 1570 | -158 | 90 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1392 |  | 1570 | -178 | 89 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1335 |  | 1570 | -235 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 735 |  | 870 | -135 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 731 |  | 870 | -139 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1319 |  | 1570 | -251 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1314 |  | 1570 | -256 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1303 |  | 1570 | -267 | 83 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1300 |  | 1570 | -270 | 83 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1293 |  | 1570 | -277 | 82 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1208 |  | 1570 | -362 | 77 | []

## 1230Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 1229
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1561 | -1570 | -1570 | -9 | 99 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1473 | -1570 | -1570 | -97 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1452 | -1570 | -1570 | -118 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1402 | -1570 | -1570 | -168 | 89 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1382 | -1570 | -1570 | -188 | 88 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 | -1570 | -1570 | -242 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1312 | -1570 | -1570 | -258 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1309 | -1570 | -1570 | -261 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 722 | 870 | 870 | -148 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1300 | -1570 | -1570 | -270 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 718 | 870 | 870 | -152 | 83 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1295 | -1570 | -1570 | -275 | 83 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1289 | -1570 | -1570 | -281 | 82 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1222 | -1570 | -1570 | -348 | 78 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1401 | 1995 | 1995 | -594 | 70 | []

## 1230Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 1229
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1561 |  | -1570 | -9 | 99 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1473 |  | -1570 | -97 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1452 |  | -1570 | -118 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1402 |  | -1570 | -168 | 89 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1382 |  | -1570 | -188 | 88 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 |  | -1570 | -242 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1312 |  | -1570 | -258 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1309 |  | -1570 | -261 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 722 |  | 870 | -148 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1300 |  | -1570 | -270 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 718 |  | 870 | -152 | 83 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1295 |  | -1570 | -275 | 83 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1289 |  | -1570 | -281 | 82 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1222 |  | -1570 | -348 | 78 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1401 |  | 1995 | -594 | 70 | []

## 1330Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 1236
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1557 | -1570 | -1570 | -13 | 99 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1466 | -1570 | -1570 | -104 | 93 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1417 | -1570 | -1570 | -153 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1401 | -1570 | -1570 | -169 | 89 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1358 | -1570 | -1570 | -212 | 86 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1323 | -1570 | -1570 | -247 | 84 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1322 | -1570 | -1570 | -248 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1307 | -1570 | -1570 | -263 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 721 | 870 | 870 | -149 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1295 | -1570 | -1570 | -275 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 717 | 870 | 870 | -153 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1290 | -1570 | -1570 | -280 | 82 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1286 | -1570 | -1570 | -284 | 82 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1215 | -1570 | -1570 | -355 | 77 | []

## 1330Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 1236
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1557 |  | -1570 | -13 | 99 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1466 |  | -1570 | -104 | 93 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1417 |  | -1570 | -153 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1401 |  | -1570 | -169 | 89 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1358 |  | -1570 | -212 | 86 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1323 |  | -1570 | -247 | 84 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1322 |  | -1570 | -248 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1307 |  | -1570 | -263 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 721 |  | 870 | -149 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1295 |  | -1570 | -275 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 717 |  | 870 | -153 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1290 |  | -1570 | -280 | 82 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1286 |  | -1570 | -284 | 82 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1215 |  | -1570 | -355 | 77 | []

## 1430Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 1028
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1569 | -1570 | -1570 | -1 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1503 | -1570 | -1570 | -67 | 96 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1427 | -1570 | -1570 | -143 | 91 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1404 | -1570 | -1570 | -166 | 89 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1371 | -1570 | -1570 | -199 | 87 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1331 | -1570 | -1570 | -239 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1329 | -1570 | -1570 | -241 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 730 | 870 | 870 | -140 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1316 | -1570 | -1570 | -254 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 726 | 870 | 870 | -144 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1304 | -1570 | -1570 | -266 | 83 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1297 | -1570 | -1570 | -273 | 83 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1293 | -1570 | -1570 | -277 | 82 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1175 | -1570 | -1570 | -395 | 75 | []

## 1430Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 1028
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1569 |  | -1570 | -1 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1503 |  | -1570 | -67 | 96 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1427 |  | -1570 | -143 | 91 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1404 |  | -1570 | -166 | 89 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1371 |  | -1570 | -199 | 87 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1331 |  | -1570 | -239 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1329 |  | -1570 | -241 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 _RRESI22 _1:line | 730 |  | 870 | -140 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1316 |  | -1570 | -254 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 _RRESI12 _1:line | 726 |  | 870 | -144 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1304 |  | -1570 | -266 | 83 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1297 |  | -1570 | -273 | 83 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1293 |  | -1570 | -277 | 82 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1175 |  | -1570 | -395 | 75 | []

## 1530Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 770
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1508 | 1570 | 1570 | -62 | 96 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1401 | 1570 | 1570 | -169 | 89 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 | 1570 | 1570 | -202 | 87 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1341 | 1570 | 1570 | -229 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1309 | 1570 | 1570 | -261 | 83 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1297 | 1570 | 1570 | -273 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1288 | 1570 | 1570 | -282 | 82 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1279 | 1570 | 1570 | -291 | 81 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1268 | 1570 | 1570 | -302 | 81 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1264 | 1570 | 1570 | -306 | 81 | []

## 1530Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 770
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1508 |  | 1570 | -62 | 96 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1401 |  | 1570 | -169 | 89 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 |  | 1570 | -202 | 87 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1341 |  | 1570 | -229 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1309 |  | 1570 | -261 | 83 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1297 |  | 1570 | -273 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1288 |  | 1570 | -282 | 82 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1279 |  | 1570 | -291 | 81 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1268 |  | 1570 | -302 | 81 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1264 |  | 1570 | -306 | 81 | []

## 1630Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 1722
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1569 | 1570 | 1570 | -1 | 100 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 | 1570 | 1570 | -85 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1455 | 1570 | 1570 | -115 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 | 1570 | 1570 | -135 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1389 | 1570 | 1570 | -181 | 88 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1356 | 1570 | 1570 | -214 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1351 | 1570 | 1570 | -219 | 86 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1346 | 1570 | 1570 | -224 | 86 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1335 | 1570 | 1570 | -235 | 85 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1335 | 1570 | 1570 | -235 | 85 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1330 | 1570 | 1570 | -240 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1325 | 1570 | 1570 | -245 | 84 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1323 | 1570 | 1570 | -247 | 84 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1478 | 1995 | 1995 | -517 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -895 | -1248 | -1248 | -353 | 72 | []

## 1630Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 1722
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1570 | -1 | 100 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 |  | 1570 | -85 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1455 |  | 1570 | -115 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1570 | -135 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1389 |  | 1570 | -181 | 88 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1356 |  | 1570 | -214 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1351 |  | 1570 | -219 | 86 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1346 |  | 1570 | -224 | 86 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1335 |  | 1570 | -235 | 85 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1335 |  | 1570 | -235 | 85 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1330 |  | 1570 | -240 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1325 |  | 1570 | -245 | 84 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1323 |  | 1570 | -247 | 84 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1478 |  | 1995 | -517 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -895 |  | -1248 | -353 | 72 | []

## 1730Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3304
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1497 | 1570 | 1570 | -73 | 95 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1497 | 1570 | 1570 | -73 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1489 | 1570 | 1570 | -81 | 95 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1869 | 1995 | 1995 | -126 | 94 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1457 | 1570 | 1570 | -113 | 93 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1450 | 1570 | 1570 | -120 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1430 | 1570 | 1570 | -140 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1429 | 1570 | 1570 | -141 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1424 | 1570 | 1570 | -146 | 91 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1423 | 1570 | 1570 | -147 | 91 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1409 | 1570 | 1570 | -161 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1408 | 1570 | 1570 | -162 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1404 | 1570 | 1570 | -166 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 | 1570 | 1570 | -170 | 89 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1778 | 1995 | 1995 | -217 | 89 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1762 | 1995 | 1995 | -233 | 88 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1751 | 1995 | 1995 | -244 | 88 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1747 | 1995 | 1995 | -248 | 88 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1743 | 1995 | 1995 | -252 | 87 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1743 | 1995 | 1995 | -252 | 87 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1742 | 1995 | 1995 | -253 | 87 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1739 | 1995 | 1995 | -256 | 87 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1737 | 1995 | 1995 | -258 | 87 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1719 | 1995 | 1995 | -276 | 86 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1715 | 1995 | 1995 | -280 | 86 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1681 | 1995 | 1995 | -314 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1655 | 1995 | 1995 | -340 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1605 | 1995 | 1995 | -390 | 80 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1591 | 1995 | 1995 | -404 | 80 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1531 | 2000 | 2000 | -469 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1528 | -2000 | -2000 | -472 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1519 | 2000 | 2000 | -481 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1516 | -2000 | -2000 | -484 | 76 | []

## 1730Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3304
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1497 |  | 1570 | -73 | 95 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1497 |  | 1570 | -73 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1489 |  | 1570 | -81 | 95 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1869 |  | 1995 | -126 | 94 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1457 |  | 1570 | -113 | 93 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1450 |  | 1570 | -120 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1430 |  | 1570 | -140 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1429 |  | 1570 | -141 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1424 |  | 1570 | -146 | 91 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1423 |  | 1570 | -147 | 91 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1409 |  | 1570 | -161 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1408 |  | 1570 | -162 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1404 |  | 1570 | -166 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 |  | 1570 | -170 | 89 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1778 |  | 1995 | -217 | 89 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1762 |  | 1995 | -233 | 88 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1751 |  | 1995 | -244 | 88 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1747 |  | 1995 | -248 | 88 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1743 |  | 1995 | -252 | 87 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1743 |  | 1995 | -252 | 87 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1742 |  | 1995 | -253 | 87 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1739 |  | 1995 | -256 | 87 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1737 |  | 1995 | -258 | 87 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1719 |  | 1995 | -276 | 86 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1715 |  | 1995 | -280 | 86 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1681 |  | 1995 | -314 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1655 |  | 1995 | -340 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1605 |  | 1995 | -390 | 80 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1591 |  | 1995 | -404 | 80 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1531 |  | 2000 | -469 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1528 |  | -2000 | -472 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1519 |  | 2000 | -481 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1516 |  | -2000 | -484 | 76 | []

## 1830Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2845
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1495 | 1570 | 1570 | -75 | 95 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1455 | 1570 | 1570 | -115 | 93 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1441 | 1570 | 1570 | -129 | 92 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1441 | 1570 | 1570 | -129 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 | 1570 | 1570 | -134 | 91 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1793 | 1995 | 1995 | -202 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1406 | 1570 | 1570 | -164 | 90 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1403 | 1570 | 1570 | -167 | 89 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 | 1570 | 1570 | -168 | 89 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1401 | 1570 | 1570 | -169 | 89 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1399 | 1570 | 1570 | -171 | 89 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1380 | 1570 | 1570 | -190 | 88 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1380 | 1570 | 1570 | -190 | 88 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1379 | 1570 | 1570 | -191 | 88 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1665 | 1995 | 1995 | -330 | 83 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1636 | 1995 | 1995 | -359 | 82 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1635 | 1995 | 1995 | -360 | 82 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1634 | 1995 | 1995 | -361 | 82 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1634 | 1995 | 1995 | -361 | 82 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1621 | 1995 | 1995 | -374 | 81 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1619 | 1995 | 1995 | -376 | 81 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1613 | 1995 | 1995 | -382 | 81 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1596 | 1995 | 1995 | -399 | 80 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1595 | 1995 | 1995 | -400 | 80 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1594 | 1995 | 1995 | -401 | 80 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1588 | 1995 | 1995 | -407 | 80 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1515 | 1995 | 1995 | -480 | 76 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1512 | 1995 | 1995 | -483 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1504 | 1995 | 1995 | -491 | 75 | []

## 1830Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2845
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1495 |  | 1570 | -75 | 95 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1455 |  | 1570 | -115 | 93 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1441 |  | 1570 | -129 | 92 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1441 |  | 1570 | -129 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 |  | 1570 | -134 | 91 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1793 |  | 1995 | -202 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1406 |  | 1570 | -164 | 90 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1403 |  | 1570 | -167 | 89 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 |  | 1570 | -168 | 89 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1401 |  | 1570 | -169 | 89 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1399 |  | 1570 | -171 | 89 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1380 |  | 1570 | -190 | 88 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1380 |  | 1570 | -190 | 88 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1379 |  | 1570 | -191 | 88 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1665 |  | 1995 | -330 | 83 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1636 |  | 1995 | -359 | 82 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1635 |  | 1995 | -360 | 82 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1634 |  | 1995 | -361 | 82 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1634 |  | 1995 | -361 | 82 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1621 |  | 1995 | -374 | 81 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1619 |  | 1995 | -376 | 81 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1613 |  | 1995 | -382 | 81 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1596 |  | 1995 | -399 | 80 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1595 |  | 1995 | -400 | 80 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1594 |  | 1995 | -401 | 80 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1588 |  | 1995 | -407 | 80 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1515 |  | 1995 | -480 | 76 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1512 |  | 1995 | -483 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1504 |  | 1995 | -491 | 75 | []

## 1930Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 1667
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1508 | 1570 | 1570 | -62 | 96 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1483 | 1570 | 1570 | -87 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 | 1570 | 1570 | -168 | 89 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1376 | 1570 | 1570 | -194 | 88 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1358 | 1570 | 1570 | -212 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1352 | 1570 | 1570 | -218 | 86 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1346 | 1570 | 1570 | -224 | 86 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1346 | 1570 | 1570 | -224 | 86 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1335 | 1570 | 1570 | -235 | 85 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1332 | 1570 | 1570 | -238 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1332 | 1570 | 1570 | -238 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1331 | 1570 | 1570 | -239 | 85 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1328 | 1570 | 1570 | -242 | 85 | []

## 1930Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 1667
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1508 |  | 1570 | -62 | 96 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1483 |  | 1570 | -87 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 |  | 1570 | -168 | 89 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1376 |  | 1570 | -194 | 88 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1358 |  | 1570 | -212 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1352 |  | 1570 | -218 | 86 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1346 |  | 1570 | -224 | 86 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1346 |  | 1570 | -224 | 86 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1335 |  | 1570 | -235 | 85 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1332 |  | 1570 | -238 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1332 |  | 1570 | -238 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1331 |  | 1570 | -239 | 85 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1328 |  | 1570 | -242 | 85 | []

## 2030Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 1658
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 | 1570 | 1570 | -3 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1509 | 1570 | 1570 | -61 | 96 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 | 1570 | 1570 | -85 | 95 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 | 1570 | 1570 | -168 | 89 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1377 | 1570 | 1570 | -193 | 88 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1357 | 1570 | 1570 | -213 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1351 | 1570 | 1570 | -219 | 86 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1345 | 1570 | 1570 | -225 | 86 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1344 | 1570 | 1570 | -226 | 86 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1334 | 1570 | 1570 | -236 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1330 | 1570 | 1570 | -240 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1329 | 1570 | 1570 | -241 | 85 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1329 | 1570 | 1570 | -241 | 85 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1326 | 1570 | 1570 | -244 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -905 | -1248 | -1248 | -343 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -904 | -1248 | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -897 | -1248 | -1248 | -352 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -896 | -1248 | -1248 | -352 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -890 | -1248 | -1248 | -359 | 71 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -888 | -1248 | -1248 | -361 | 71 | []

## 2030Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 1658
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 |  | 1570 | -3 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1509 |  | 1570 | -61 | 96 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 |  | 1570 | -85 | 95 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 |  | 1570 | -168 | 89 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1377 |  | 1570 | -193 | 88 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1357 |  | 1570 | -213 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1351 |  | 1570 | -219 | 86 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1345 |  | 1570 | -225 | 86 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1344 |  | 1570 | -226 | 86 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1334 |  | 1570 | -236 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1330 |  | 1570 | -240 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1329 |  | 1570 | -241 | 85 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1329 |  | 1570 | -241 | 85 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1326 |  | 1570 | -244 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -905 |  | -1248 | -343 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -904 |  | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -897 |  | -1248 | -352 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -896 |  | -1248 | -352 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -890 |  | -1248 | -359 | 71 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -888 |  | -1248 | -361 | 71 | []

## 2130Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 1586
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1497 | 1570 | 1570 | -73 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1481 | 1570 | 1570 | -89 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 | 1570 | 1570 | -143 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1392 | 1570 | 1570 | -178 | 89 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1365 | 1570 | 1570 | -205 | 87 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1348 | 1570 | 1570 | -222 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1340 | 1570 | 1570 | -230 | 85 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1328 | 1570 | 1570 | -242 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1320 | 1570 | 1570 | -250 | 84 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1315 | 1570 | 1570 | -255 | 84 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1314 | 1570 | 1570 | -256 | 84 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1314 | 1570 | 1570 | -256 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -888 | -1248 | -1248 | -361 | 71 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -886 | -1248 | -1248 | -362 | 71 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -879 | -1248 | -1248 | -369 | 70 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -879 | -1248 | -1248 | -369 | 70 | []

## 2130Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 1586
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1497 |  | 1570 | -73 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1481 |  | 1570 | -89 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1570 | -143 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1392 |  | 1570 | -178 | 89 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1365 |  | 1570 | -205 | 87 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1348 |  | 1570 | -222 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1340 |  | 1570 | -230 | 85 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1328 |  | 1570 | -242 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1320 |  | 1570 | -250 | 84 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1315 |  | 1570 | -255 | 84 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1314 |  | 1570 | -256 | 84 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1314 |  | 1570 | -256 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -888 |  | -1248 | -361 | 71 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -886 |  | -1248 | -362 | 71 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -879 |  | -1248 | -369 | 70 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -879 |  | -1248 | -369 | 70 | []

## 2230Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2214
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1570 | 1570 | 1570 | 0 | 100 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1482 | 1570 | 1570 | -88 | 94 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1472 | 1570 | 1570 | -98 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1406 | 1570 | 1570 | -164 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1374 | 1570 | 1570 | -196 | 87 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1369 | 1570 | 1570 | -201 | 87 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1369 | 1570 | 1570 | -201 | 87 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1367 | 1570 | 1570 | -203 | 87 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1361 | 1570 | 1570 | -209 | 87 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1356 | 1570 | 1570 | -214 | 86 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1355 | 1570 | 1570 | -215 | 86 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1340 | 1570 | 1570 | -230 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1340 | 1570 | 1570 | -230 | 85 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1338 | 1570 | 1570 | -232 | 85 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1429 | 1995 | 1995 | -566 | 72 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1420 | 1995 | 1995 | -575 | 71 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1412 | 1995 | 1995 | -583 | 71 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1405 | 1995 | 1995 | -590 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2214
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1570 |  | 1570 | 0 | 100 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1482 |  | 1570 | -88 | 94 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1472 |  | 1570 | -98 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1406 |  | 1570 | -164 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1374 |  | 1570 | -196 | 87 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1369 |  | 1570 | -201 | 87 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1369 |  | 1570 | -201 | 87 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1367 |  | 1570 | -203 | 87 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1361 |  | 1570 | -209 | 87 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1356 |  | 1570 | -214 | 86 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1355 |  | 1570 | -215 | 86 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1340 |  | 1570 | -230 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1340 |  | 1570 | -230 | 85 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1338 |  | 1570 | -232 | 85 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1429 |  | 1995 | -566 | 72 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1420 |  | 1995 | -575 | 71 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1412 |  | 1995 | -583 | 71 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1405 |  | 1995 | -590 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3333
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1496 | 1570 | 1570 | -74 | 95 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1484 | 1570 | 1570 | -86 | 94 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1484 | 1570 | 1570 | -86 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 | 1570 | 1570 | -119 | 92 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1448 | 1570 | 1570 | -122 | 92 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1423 | 1570 | 1570 | -147 | 91 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1421 | 1570 | 1570 | -149 | 90 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1420 | 1570 | 1570 | -150 | 90 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1420 | 1570 | 1570 | -150 | 90 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1800 | 1995 | 1995 | -195 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1410 | 1570 | 1570 | -160 | 90 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 | 1570 | 1570 | -170 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1398 | 1570 | 1570 | -172 | 89 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1774 | 1995 | 1995 | -221 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1394 | 1570 | 1570 | -176 | 89 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1758 | 1995 | 1995 | -237 | 88 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1755 | 1995 | 1995 | -240 | 88 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1739 | 1995 | 1995 | -256 | 87 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1715 | 1995 | 1995 | -280 | 86 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1706 | 1995 | 1995 | -289 | 86 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1706 | 1995 | 1995 | -289 | 86 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1696 | 1995 | 1995 | -299 | 85 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1690 | 1995 | 1995 | -305 | 85 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1675 | 1995 | 1995 | -320 | 84 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1674 | 1995 | 1995 | -321 | 84 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1652 | 1995 | 1995 | -343 | 83 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1641 | 1995 | 1995 | -354 | 82 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1643 | 2000 | 2000 | -357 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1639 | -2000 | -2000 | -361 | 82 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1628 | 2000 | 2000 | -372 | 81 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1625 | -2000 | -2000 | -375 | 81 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1532 | 1995 | 1995 | -463 | 77 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1513 | 1995 | 1995 | -482 | 76 | []

## 2330Curative
Detailed results
Generated at: | 2026-07-15 20:10
Business day: | 16.07.2026
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3333
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1496 |  | 1570 | -74 | 95 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1484 |  | 1570 | -86 | 94 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1484 |  | 1570 | -86 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 |  | 1570 | -119 | 92 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1448 |  | 1570 | -122 | 92 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1423 |  | 1570 | -147 | 91 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1421 |  | 1570 | -149 | 90 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1420 |  | 1570 | -150 | 90 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1420 |  | 1570 | -150 | 90 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1800 |  | 1995 | -195 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1410 |  | 1570 | -160 | 90 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 |  | 1570 | -170 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1398 |  | 1570 | -172 | 89 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1774 |  | 1995 | -221 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1394 |  | 1570 | -176 | 89 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1758 |  | 1995 | -237 | 88 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1755 |  | 1995 | -240 | 88 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1739 |  | 1995 | -256 | 87 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1715 |  | 1995 | -280 | 86 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1706 |  | 1995 | -289 | 86 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1706 |  | 1995 | -289 | 86 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1696 |  | 1995 | -299 | 85 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1690 |  | 1995 | -305 | 85 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1675 |  | 1995 | -320 | 84 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1674 |  | 1995 | -321 | 84 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1652 |  | 1995 | -343 | 83 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1641 |  | 1995 | -354 | 82 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1643 |  | 2000 | -357 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1639 |  | -2000 | -361 | 82 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1628 |  | 2000 | -372 | 81 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1625 |  | -2000 | -375 | 81 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1532 |  | 1995 | -463 | 77 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1513 |  | 1995 | -482 | 76 | []