## NGR borders-exports
SUBMISSION DATE: | 15.07.2026
BUSINESS DATE: | 16.07.2026
1st ID CC Results
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC North Greece | NTC North Greece | NTC GR-BG
00:00 | 01:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3694 | 3294 | 1515
01:00 | 02:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3630 | 3230 | 1485
02:00 | 03:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3432 | 3032 | 1394
03:00 | 04:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3488 | 3088 | 1420
04:00 | 05:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3490 | 3090 | 1421
05:00 | 06:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3539 | 3139 | 1444
06:00 | 07:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3531 | 3131 | 1440
07:00 | 08:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3392 | 2992 | 1376
08:00 | 09:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3077 | 2677 | 1231
09:00 | 10:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 2976 | 2576 | 1184
10:00 | 11:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 2957 | 2557 | 1176
11:00 | 12:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 2987 | 2587 | 1190
12:00 | 13:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 2957 | 2557 | 1176
13:00 | 14:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 2926 | 2526 | 1162
14:00 | 15:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 2713 | 2313 | 1063
15:00 | 16:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 2636 | 2236 | 1028
16:00 | 17:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3120 | 2720 | 1251
17:00 | 18:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3405 | 3005 | 1382
18:00 | 19:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3423 | 3023 | 1390
19:00 | 20:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3171 | 2771 | 1274
20:00 | 21:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3215 | 2815 | 1294
21:00 | 22:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3299 | 2899 | 1333
22:00 | 23:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3345 | 2945 | 1354
23:00 | 00:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | 100 | 3642 | 3242 | 1491

## NGR borders-imports
SUBMISSION DATE: | 15.07.2026
BUSINESS DATE: | 16.07.2026
1st ID CC Results
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC North Greece | NTC North Greece | NTC BG-GR
00:00 | 01:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3271 | 2871 | 1406
01:00 | 02:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3351 | 2951 | 1446
02:00 | 03:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3445 | 3045 | 1491
03:00 | 04:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3442 | 3042 | 1490
04:00 | 05:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3424 | 3024 | 1481
05:00 | 06:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3443 | 3043 | 1491
06:00 | 07:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3394 | 2994 | 1466
07:00 | 08:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3459 | 3059 | 1498
08:00 | 09:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3567 | 3167 | 1551
09:00 | 10:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3445 | 3045 | 1492
10:00 | 11:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3437 | 3037 | 1487
11:00 | 12:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3420 | 3020 | 1480
12:00 | 13:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3421 | 3021 | 1480
13:00 | 14:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3486 | 3086 | 1512
14:00 | 15:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3707 | 3307 | 1620
15:00 | 16:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3758 | 3358 | 1645
16:00 | 17:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3462 | 3062 | 1500
17:00 | 18:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3377 | 2977 | 1458
18:00 | 19:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3452 | 3052 | 1495
19:00 | 20:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3689 | 3289 | 1611
20:00 | 21:00 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | 100 | 3716 | 3316 | 1624
21:00 | 22:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3653 | 3253 | 1593
22:00 | 23:00 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3618 | 3218 | 1576
23:00 | 00:00 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | 100 | 3308 | 2908 | 1424

## NGR borders-exports RAs
SUBMISSION DATE: | 15.07.2026
BUSINESS DATE: | 16.07.2026
1st ID CC Remedial Actions
Name of the RA | RA ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30

## NGR borders-imports RAs
SUBMISSION DATE: | 15.07.2026
BUSINESS DATE: | 16.07.2026
1st ID CC Remedial Actions
Name of the RA | RA ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30