## 0030
Detailed results
Generated at: | 14/07/2026 21:21:33
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3409.28
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1592 | 1587 | 5 | 100 | -1122 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1570 | 1587 | -17 | 99 | -1100 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1488 | 1587 | -99 | 94 | -1046 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1480 | 1587 | -107 | 93 | -1035 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1485 | 1600 | -115 | 93 | -1043 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1412 | 1587 | -175 | 89 | -995 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1407 | 1587 | -180 | 89 | -993 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1392 | 1587 | -195 | 88 | -961 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1392 | 1587 | -195 | 88 | -961 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1365 | 1587 | -222 | 86 | -962 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1357 | 1600 | -243 | 85 | -907 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1344 | 1587 | -243 | 85 | -949 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1270 | 1587 | -317 | 80 | -899 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1587 | -333 | 79 | -886 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1252 | 1587 | -335 | 79 | -886 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1259 | 1600 | -341 | 79 | -891 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1587 | -367 | 77 | -866 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1587 | -368 | 77 | -863 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1587 | -376 | 76 | -858 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -858 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -857 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1587 | -380 | 76 | -856 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1587 | -380 | 76 | -856 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1587 | -381 | 76 | -856 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1587 | -382 | 76 | -855 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1587 | -383 | 76 | -854 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1587 | -384 | 76 | -853 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -385 | 76 | -852 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -385 | 76 | -852 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1587 | -388 | 76 | -850 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1587 | -388 | 76 | -850 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1587 | -394 | 75 | -846 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -845 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1587 | -400 | 75 | -842 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1587 | -404 | 75 | -836 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1587 | -405 | 74 | -840 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1587 | -407 | 74 | -838 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1179 | 1600 | -421 | 74 | -798 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1125 | 1587 | -462 | 71 | -795 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1587 | -465 | 71 | -797 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1117 | 1587 | -470 | 70 | -796 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1116 | 1587 | -470 | 70 | -796 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1113 | 1587 | -474 | 70 | -792 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1112 | 1587 | -475 | 70 | -790 | AC

## 0130
Detailed results
Generated at: | 14/07/2026 21:21:33
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3427.27
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1595 | 1587 | 8 | 100 | -1126 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1553 | 1587 | -34 | 98 | -1089 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1484 | 1587 | -103 | 94 | -1038 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1488 | 1600 | -112 | 93 | -1046 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1471 | 1587 | -116 | 93 | -1035 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1414 | 1587 | -173 | 89 | -998 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1412 | 1587 | -175 | 89 | -997 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1400 | 1587 | -187 | 88 | -967 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1400 | 1587 | -187 | 88 | -967 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1389 | 1600 | -211 | 87 | -925 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1369 | 1587 | -218 | 86 | -966 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1345 | 1587 | -242 | 85 | -951 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1587 | -321 | 80 | -897 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1587 | -333 | 79 | -886 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1252 | 1587 | -335 | 79 | -887 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1259 | 1600 | -341 | 79 | -893 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -866 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -863 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1587 | -373 | 76 | -862 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -858 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1587 | -380 | 76 | -858 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1587 | -380 | 76 | -857 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1587 | -381 | 76 | -856 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1587 | -382 | 76 | -856 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1587 | -384 | 76 | -855 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1587 | -384 | 76 | -854 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1212 | 1600 | -388 | 76 | -819 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1587 | -386 | 76 | -853 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1587 | -387 | 76 | -852 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1587 | -387 | 76 | -852 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -850 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -850 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1587 | -398 | 75 | -845 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1587 | -398 | 75 | -845 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1587 | -402 | 75 | -842 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1587 | -406 | 74 | -841 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1587 | -407 | 74 | -835 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1587 | -409 | 74 | -837 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1587 | -461 | 71 | -801 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1587 | -466 | 71 | -794 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1118 | 1587 | -469 | 70 | -798 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1117 | 1587 | -470 | 70 | -798 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1121 | 1600 | -479 | 70 | -762 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1121 | 1600 | -479 | 70 | -760 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1120 | 1600 | -480 | 70 | -760 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1111 | 1587 | -476 | 70 | -792 | AC

## 0230
Detailed results
Generated at: | 14/07/2026 21:21:33
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3468.12
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1594 | 1587 | 7 | 100 | -1126 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1547 | 1587 | -40 | 97 | -1086 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1484 | 1587 | -103 | 94 | -1038 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1464 | 1587 | -123 | 92 | -1031 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1472 | 1600 | -128 | 92 | -1036 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1412 | 1587 | -175 | 89 | -997 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1406 | 1587 | -181 | 89 | -972 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1406 | 1587 | -181 | 89 | -972 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1411 | 1600 | -189 | 88 | -939 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1399 | 1587 | -188 | 88 | -989 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1367 | 1587 | -220 | 86 | -965 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1342 | 1587 | -245 | 85 | -949 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1260 | 1587 | -327 | 79 | -894 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1247 | 1587 | -340 | 79 | -885 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1256 | 1600 | -344 | 79 | -891 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1587 | -342 | 78 | -881 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1235 | 1600 | -365 | 77 | -833 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -863 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1587 | -376 | 76 | -860 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -859 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1587 | -379 | 76 | -858 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -385 | 76 | -854 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -385 | 76 | -854 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1587 | -386 | 76 | -853 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1587 | -387 | 76 | -853 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1587 | -388 | 76 | -853 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1587 | -389 | 75 | -851 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1587 | -391 | 75 | -850 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1587 | -393 | 75 | -849 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1587 | -393 | 75 | -849 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -847 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -847 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1587 | -403 | 75 | -842 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1587 | -404 | 75 | -841 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1587 | -410 | 74 | -838 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1587 | -412 | 74 | -837 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1587 | -413 | 74 | -835 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1587 | -415 | 74 | -830 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1143 | 1600 | -457 | 71 | -777 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1136 | 1600 | -464 | 71 | -770 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1135 | 1600 | -465 | 71 | -769 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1119 | 1587 | -468 | 70 | -793 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1116 | 1587 | -471 | 70 | -795 | AC

## 0330
Detailed results
Generated at: | 14/07/2026 21:21:33
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3451.57
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1595 | 1587 | 8 | 100 | -1127 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1542 | 1587 | -45 | 97 | -1084 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1480 | 1587 | -107 | 93 | -1037 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1473 | 1600 | -127 | 92 | -1037 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1460 | 1587 | -127 | 92 | -1029 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1410 | 1587 | -177 | 89 | -997 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1405 | 1587 | -182 | 89 | -972 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1405 | 1587 | -182 | 89 | -972 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1400 | 1587 | -187 | 88 | -991 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1390 | 1600 | -210 | 87 | -926 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1371 | 1587 | -216 | 86 | -968 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1341 | 1587 | -246 | 84 | -950 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1587 | -330 | 79 | -893 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1249 | 1587 | -338 | 79 | -887 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1600 | -343 | 79 | -893 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1247 | 1587 | -340 | 79 | -883 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1225 | 1600 | -375 | 77 | -827 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1587 | -373 | 77 | -864 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1587 | -373 | 76 | -864 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -862 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1587 | -382 | 76 | -857 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1587 | -384 | 76 | -856 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1587 | -384 | 76 | -856 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -385 | 76 | -855 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1587 | -386 | 76 | -855 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1587 | -387 | 76 | -854 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1587 | -388 | 76 | -853 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1587 | -389 | 75 | -852 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1587 | -391 | 75 | -851 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1587 | -391 | 75 | -851 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1587 | -394 | 75 | -849 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1587 | -394 | 75 | -849 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1587 | -402 | 75 | -844 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1587 | -402 | 75 | -843 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1587 | -407 | 74 | -840 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1587 | -409 | 74 | -840 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1587 | -412 | 74 | -833 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1587 | -412 | 74 | -837 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1587 | -464 | 71 | -801 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1587 | -466 | 71 | -795 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1125 | 1600 | -475 | 70 | -765 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1114 | 1587 | -473 | 70 | -796 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1122 | 1600 | -478 | 70 | -761 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1122 | 1600 | -478 | 70 | -761 | AC

## 0430
Detailed results
Generated at: | 14/07/2026 21:21:34
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3483.3
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1592 | 1587 | 5 | 100 | -1125 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1543 | 1587 | -44 | 97 | -1085 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1490 | 1587 | -97 | 94 | -1041 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1471 | 1600 | -129 | 92 | -1036 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1458 | 1587 | -129 | 92 | -1029 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1431 | 1600 | -169 | 89 | -950 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1411 | 1587 | -176 | 89 | -998 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1406 | 1587 | -181 | 89 | -973 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1405 | 1587 | -182 | 89 | -973 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1399 | 1587 | -188 | 88 | -990 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1371 | 1587 | -216 | 86 | -968 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1341 | 1587 | -246 | 84 | -950 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1587 | -333 | 79 | -891 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1260 | 1600 | -340 | 79 | -894 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1587 | -342 | 78 | -884 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1587 | -342 | 78 | -881 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1253 | 1600 | -347 | 78 | -844 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -862 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -861 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -859 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1587 | -381 | 76 | -857 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1587 | -386 | 76 | -855 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1587 | -387 | 76 | -854 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1587 | -389 | 75 | -852 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -852 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -852 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1587 | -392 | 75 | -851 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1587 | -393 | 75 | -850 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -848 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -848 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1587 | -398 | 75 | -846 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1587 | -399 | 75 | -846 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1587 | -406 | 74 | -840 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1587 | -408 | 74 | -840 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1587 | -412 | 74 | -837 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1587 | -414 | 74 | -837 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1587 | -417 | 74 | -834 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1587 | -418 | 74 | -829 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1160 | 1600 | -440 | 73 | -787 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1148 | 1600 | -452 | 72 | -777 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1148 | 1600 | -452 | 72 | -777 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1142 | 1600 | -458 | 71 | -672 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1116 | 1587 | -471 | 70 | -792 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1115 | 1587 | -472 | 70 | -795 | AC

## 0530
Detailed results
Generated at: | 14/07/2026 21:21:34
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3503.51
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1598 | 1587 | 11 | 101 | -1128 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1565 | 1587 | -22 | 99 | -1098 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1497 | 1587 | -90 | 94 | -1047 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1478 | 1587 | -109 | 93 | -1040 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1486 | 1600 | -114 | 93 | -1045 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1417 | 1587 | -170 | 89 | -1000 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1415 | 1587 | -172 | 89 | -1000 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1402 | 1587 | -185 | 88 | -968 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1402 | 1587 | -185 | 88 | -968 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1411 | 1600 | -189 | 88 | -936 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1385 | 1587 | -202 | 87 | -977 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1346 | 1587 | -241 | 85 | -952 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1587 | -323 | 80 | -897 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1270 | 1600 | -330 | 79 | -900 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1255 | 1587 | -332 | 79 | -888 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1252 | 1587 | -335 | 79 | -888 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1246 | 1600 | -354 | 78 | -837 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1587 | -366 | 77 | -867 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1587 | -367 | 77 | -865 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1587 | -368 | 77 | -867 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -861 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -860 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -859 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -859 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -859 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1587 | -381 | 76 | -857 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1587 | -384 | 76 | -855 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -384 | 76 | -854 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -385 | 76 | -854 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1587 | -389 | 76 | -851 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -851 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -850 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1587 | -394 | 75 | -848 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1587 | -399 | 75 | -844 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1587 | -399 | 75 | -844 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1587 | -402 | 75 | -844 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1587 | -404 | 75 | -838 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1587 | -408 | 74 | -838 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1130 | 1587 | -457 | 71 | -805 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1124 | 1587 | -463 | 71 | -797 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1130 | 1600 | -470 | 71 | -764 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1129 | 1600 | -471 | 71 | -762 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1129 | 1600 | -471 | 71 | -762 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1118 | 1587 | -469 | 70 | -798 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1113 | 1587 | -474 | 70 | -793 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1111 | 1587 | -476 | 70 | -794 | AC

## 0630
Detailed results
Generated at: | 14/07/2026 21:21:34
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3462.62
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1589 | 1587 | 2 | 100 | -1122 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1538 | 1587 | -49 | 97 | -1083 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1512 | 1587 | -75 | 95 | -1062 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1508 | 1600 | -92 | 94 | -1064 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1461 | 1587 | -126 | 92 | -1030 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1445 | 1587 | -142 | 91 | -1019 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1430 | 1587 | -157 | 90 | -1008 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1416 | 1587 | -171 | 89 | -998 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1416 | 1600 | -184 | 89 | -938 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1362 | 1587 | -225 | 86 | -943 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1361 | 1587 | -226 | 86 | -944 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1355 | 1587 | -232 | 85 | -957 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1289 | 1600 | -311 | 81 | -912 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1275 | 1587 | -312 | 80 | -901 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1274 | 1587 | -313 | 80 | -901 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1587 | -323 | 80 | -895 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1265 | 1600 | -335 | 79 | -844 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1250 | 1587 | -337 | 79 | -886 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1587 | -350 | 78 | -876 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1587 | -352 | 78 | -876 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1587 | -354 | 78 | -873 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1232 | 1587 | -355 | 78 | -873 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1587 | -362 | 77 | -868 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1224 | 1587 | -363 | 77 | -868 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1587 | -364 | 77 | -866 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1587 | -367 | 77 | -865 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -861 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -858 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -861 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -860 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -858 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -858 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -859 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -857 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1587 | -382 | 76 | -854 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -385 | 76 | -857 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -385 | 76 | -852 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1587 | -398 | 75 | -847 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1587 | -401 | 75 | -842 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1587 | -409 | 74 | -836 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1587 | -425 | 73 | -828 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1170 | 1600 | -430 | 73 | -791 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1131 | 1587 | -456 | 71 | -800 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1130 | 1587 | -457 | 71 | -803 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1139 | 1600 | -461 | 71 | -737 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1126 | 1600 | -474 | 70 | -756 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1117 | 1587 | -470 | 70 | -794 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1126 | 1600 | -474 | 70 | -756 | AC

## 0730
Detailed results
Generated at: | 14/07/2026 21:21:34
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3473.27
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1594 | 1587 | 7 | 100 | -1123 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1538 | 1587 | -49 | 97 | -1078 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1537 | 1600 | -63 | 96 | -1082 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1493 | 1587 | -94 | 94 | -1051 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1470 | 1587 | -117 | 93 | -1035 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1469 | 1600 | -131 | 92 | -968 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1449 | 1587 | -138 | 91 | -1019 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1447 | 1587 | -140 | 91 | -1018 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1419 | 1587 | -168 | 89 | -1001 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1361 | 1587 | -226 | 86 | -960 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1357 | 1587 | -230 | 85 | -936 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1356 | 1587 | -231 | 85 | -937 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1331 | 1600 | -269 | 83 | -884 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1313 | 1587 | -274 | 83 | -932 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1300 | 1587 | -287 | 82 | -923 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1308 | 1600 | -292 | 82 | -923 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1290 | 1587 | -297 | 81 | -910 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1288 | 1587 | -299 | 81 | -910 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1277 | 1587 | -310 | 80 | -903 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1284 | 1600 | -316 | 80 | -875 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1253 | 1587 | -334 | 79 | -886 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1250 | 1587 | -337 | 79 | -883 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1587 | -342 | 78 | -882 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1244 | 1587 | -343 | 78 | -880 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1243 | 1587 | -344 | 78 | -880 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1242 | 1587 | -345 | 78 | -880 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1587 | -348 | 78 | -873 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1587 | -349 | 78 | -875 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1587 | -350 | 78 | -875 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1587 | -352 | 78 | -874 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1587 | -353 | 78 | -873 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1587 | -356 | 78 | -871 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1587 | -359 | 77 | -870 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1587 | -361 | 77 | -867 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1587 | -366 | 77 | -864 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -862 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -862 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -862 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -858 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1587 | -381 | 76 | -853 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1208 | 1600 | -392 | 75 | -809 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -847 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1587 | -413 | 74 | -831 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1153 | 1600 | -447 | 72 | -772 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1153 | 1600 | -447 | 72 | -772 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1141 | 1587 | -446 | 72 | -809 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1137 | 1587 | -450 | 72 | -802 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1120 | 1587 | -467 | 71 | -795 | AC

## 0830
Detailed results
Generated at: | 14/07/2026 21:21:34
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3453.46
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2/[GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1591 | 1600 | -9 | 99 | -1032 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1517 | 1587 | -70 | 96 | -1067 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1514 | 1587 | -73 | 95 | -1057 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1488 | 1600 | -112 | 93 | -1045 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1469 | 1600 | -131 | 92 | -992 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1461 | 1600 | -139 | 91 | -956 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1433 | 1587 | -154 | 90 | -1007 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1425 | 1587 | -162 | 90 | -999 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1404 | 1587 | -183 | 88 | -985 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1384 | 1600 | -216 | 87 | -906 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1361 | 1587 | -226 | 86 | -958 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1312 | 1587 | -275 | 83 | -923 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1310 | 1587 | -277 | 83 | -927 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1301 | 1587 | -286 | 82 | -916 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1299 | 1587 | -288 | 82 | -920 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1287 | 1587 | -300 | 81 | -886 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1286 | 1587 | -301 | 81 | -886 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1265 | 1600 | -335 | 79 | -891 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1241 | 1587 | -346 | 78 | -874 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1587 | -349 | 78 | -872 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1587 | -357 | 77 | -867 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1224 | 1600 | -376 | 76 | -807 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -854 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1215 | 1600 | -385 | 76 | -804 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1215 | 1600 | -385 | 76 | -804 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1209 | 1600 | -391 | 76 | -800 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1587 | -392 | 75 | -843 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1587 | -396 | 75 | -840 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1587 | -396 | 75 | -845 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1587 | -397 | 75 | -842 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1200 | 1600 | -400 | 75 | -792 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1587 | -397 | 75 | -840 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1587 | -397 | 75 | -836 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1587 | -403 | 75 | -836 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1587 | -403 | 75 | -836 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1587 | -404 | 75 | -836 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1587 | -404 | 75 | -835 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1587 | -408 | 74 | -832 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1587 | -409 | 74 | -834 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1587 | -412 | 74 | -830 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1587 | -416 | 74 | -827 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1180 | 1600 | -420 | 74 | -779 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1172 | 1600 | -428 | 73 | -783 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1587 | -425 | 73 | -819 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1587 | -426 | 73 | -819 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1587 | -427 | 73 | -819 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1587 | -432 | 73 | -816 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1587 | -434 | 73 | -814 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1150 | 1600 | -450 | 72 | -762 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1137 | 1587 | -450 | 72 | -803 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1132 | 1600 | -468 | 71 | -749 | AC

## 0930
Detailed results
Generated at: | 14/07/2026 21:21:34
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3413.86
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1589 | 1587 | 2 | 100 | -1120 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1510 | 1600 | -90 | 94 | -1064 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1493 | 1587 | -94 | 94 | -1047 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1464 | 1587 | -123 | 92 | -1029 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1437 | 1587 | -150 | 91 | -1014 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1428 | 1587 | -159 | 90 | -1006 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1416 | 1587 | -171 | 89 | -1000 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1380 | 1587 | -207 | 87 | -979 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1383 | 1600 | -217 | 86 | -933 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1370 | 1587 | -217 | 86 | -972 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1356 | 1587 | -231 | 85 | -938 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1367 | 1600 | -233 | 85 | -861 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1355 | 1587 | -232 | 85 | -939 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1351 | 1587 | -236 | 85 | -954 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1361 | 1600 | -239 | 85 | -906 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1349 | 1587 | -238 | 85 | -952 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1328 | 1600 | -272 | 83 | -886 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1307 | 1600 | -293 | 82 | -923 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1287 | 1587 | -300 | 81 | -909 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1278 | 1587 | -309 | 81 | -904 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1274 | 1587 | -313 | 80 | -900 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1587 | -323 | 80 | -896 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1587 | -348 | 78 | -877 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1587 | -348 | 78 | -879 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1587 | -349 | 78 | -876 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1587 | -350 | 78 | -876 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1587 | -352 | 78 | -872 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1587 | -354 | 78 | -878 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1587 | -357 | 77 | -871 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1587 | -358 | 77 | -871 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1587 | -358 | 77 | -870 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1587 | -359 | 77 | -870 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1587 | -361 | 77 | -868 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1224 | 1587 | -363 | 77 | -869 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1587 | -366 | 77 | -865 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -863 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -863 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -857 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -856 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1587 | -381 | 76 | -855 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -845 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1587 | -406 | 74 | -837 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1587 | -426 | 73 | -822 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1138 | 1587 | -449 | 72 | -804 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1587 | -452 | 72 | -805 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1120 | 1587 | -468 | 71 | -795 | AC

## 1030
Detailed results
Generated at: | 14/07/2026 21:21:34
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3371.43
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1590 | 1587 | 3 | 100 | -1120 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1506 | 1600 | -94 | 94 | -1062 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1480 | 1587 | -107 | 93 | -1039 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1457 | 1587 | -130 | 92 | -1024 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1430 | 1587 | -157 | 90 | -1009 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1423 | 1587 | -164 | 90 | -1004 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1422 | 1587 | -165 | 90 | -1002 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1386 | 1587 | -201 | 87 | -983 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1376 | 1587 | -211 | 87 | -976 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1374 | 1600 | -226 | 86 | -834 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1358 | 1587 | -229 | 86 | -940 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1357 | 1587 | -230 | 86 | -940 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1352 | 1587 | -235 | 85 | -955 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1345 | 1587 | -242 | 85 | -949 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1334 | 1600 | -266 | 83 | -896 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1307 | 1600 | -293 | 82 | -876 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1304 | 1600 | -296 | 81 | -921 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1287 | 1587 | -300 | 81 | -909 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1279 | 1587 | -308 | 81 | -905 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1273 | 1587 | -314 | 80 | -899 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1281 | 1600 | -319 | 80 | -860 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1267 | 1587 | -320 | 80 | -897 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1587 | -348 | 78 | -877 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1587 | -348 | 78 | -878 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1587 | -349 | 78 | -876 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1587 | -350 | 78 | -876 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1236 | 1587 | -351 | 78 | -873 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1587 | -353 | 78 | -879 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1587 | -357 | 78 | -872 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1587 | -358 | 77 | -870 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1587 | -359 | 77 | -869 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1587 | -361 | 77 | -868 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1587 | -361 | 77 | -868 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1587 | -362 | 77 | -869 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1587 | -366 | 77 | -865 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1587 | -367 | 77 | -864 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -863 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -860 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1587 | -376 | 76 | -857 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1587 | -379 | 76 | -856 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1587 | -396 | 75 | -844 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1587 | -408 | 74 | -835 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1587 | -424 | 73 | -823 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1163 | 1600 | -437 | 73 | -650 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1142 | 1587 | -445 | 72 | -806 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1587 | -452 | 72 | -805 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1127 | 1587 | -460 | 71 | -800 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1114 | 1587 | -472 | 70 | -788 | AC

## 1130
Detailed results
Generated at: | 14/07/2026 21:21:34
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3305.31
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1586 | 1587 | -1 | 100 | -1117 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1484 | 1600 | -116 | 93 | -1046 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1456 | 1587 | -131 | 92 | -1023 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1429 | 1587 | -158 | 90 | -1005 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1420 | 1587 | -167 | 89 | -1002 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1405 | 1587 | -182 | 88 | -990 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1398 | 1587 | -189 | 88 | -987 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1372 | 1587 | -215 | 86 | -973 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1366 | 1587 | -221 | 86 | -945 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1365 | 1587 | -222 | 86 | -945 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1361 | 1587 | -226 | 86 | -966 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1346 | 1587 | -241 | 85 | -951 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1328 | 1587 | -259 | 84 | -938 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1291 | 1600 | -309 | 81 | -785 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1286 | 1600 | -314 | 80 | -909 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1271 | 1587 | -316 | 80 | -898 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1587 | -323 | 80 | -894 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1587 | -329 | 79 | -888 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1587 | -333 | 79 | -888 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1261 | 1600 | -339 | 79 | -848 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1252 | 1600 | -348 | 78 | -840 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1587 | -361 | 77 | -869 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1587 | -361 | 77 | -868 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1587 | -362 | 77 | -867 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1587 | -362 | 77 | -867 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1224 | 1587 | -363 | 77 | -864 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1228 | 1600 | -372 | 77 | -827 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -868 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1587 | -370 | 77 | -863 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1587 | -371 | 77 | -861 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -861 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -860 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1587 | -373 | 76 | -860 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1587 | -375 | 76 | -860 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -856 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -857 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1587 | -381 | 76 | -854 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1587 | -383 | 76 | -853 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1587 | -387 | 76 | -849 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -848 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1587 | -407 | 74 | -837 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1168 | 1587 | -419 | 74 | -827 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1587 | -432 | 73 | -817 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1587 | -455 | 71 | -799 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1587 | -464 | 71 | -796 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1587 | -466 | 71 | -796 | AC

## 1230
Detailed results
Generated at: | 14/07/2026 21:21:35
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3305.07
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1584 | 1587 | -3 | 100 | -1116 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1482 | 1600 | -118 | 93 | -1045 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1456 | 1587 | -131 | 92 | -1022 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1426 | 1587 | -161 | 90 | -1006 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1426 | 1587 | -161 | 90 | -1003 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1399 | 1587 | -188 | 88 | -985 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1391 | 1587 | -196 | 88 | -981 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1366 | 1587 | -221 | 86 | -944 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1365 | 1587 | -222 | 86 | -944 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1364 | 1587 | -223 | 86 | -967 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1353 | 1587 | -234 | 85 | -960 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1352 | 1587 | -235 | 85 | -955 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1328 | 1587 | -259 | 84 | -937 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1272 | 1587 | -315 | 80 | -898 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1279 | 1600 | -321 | 80 | -903 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1260 | 1587 | -327 | 79 | -891 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1256 | 1587 | -331 | 79 | -887 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1263 | 1600 | -337 | 79 | -805 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1251 | 1587 | -336 | 79 | -885 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1245 | 1600 | -355 | 78 | -838 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1587 | -362 | 77 | -868 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1224 | 1587 | -363 | 77 | -866 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1233 | 1600 | -367 | 77 | -832 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1587 | -364 | 77 | -866 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1587 | -364 | 77 | -865 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1587 | -365 | 77 | -863 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -861 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -860 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1587 | -375 | 76 | -858 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1587 | -375 | 76 | -858 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1587 | -375 | 76 | -858 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1587 | -376 | 76 | -862 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1587 | -378 | 76 | -857 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1587 | -380 | 76 | -855 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1587 | -380 | 76 | -855 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1587 | -384 | 76 | -852 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1587 | -384 | 76 | -851 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1587 | -388 | 76 | -849 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1208 | 1600 | -392 | 75 | -815 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1587 | -392 | 75 | -847 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1587 | -408 | 74 | -835 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1168 | 1587 | -419 | 74 | -827 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1587 | -432 | 73 | -817 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1129 | 1587 | -458 | 71 | -797 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1587 | -464 | 71 | -796 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1587 | -466 | 71 | -795 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1112 | 1587 | -475 | 70 | -785 | AC

## 1330
Detailed results
Generated at: | 14/07/2026 21:21:35
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3432.24
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1591 | 1587 | 4 | 100 | -1118 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1501 | 1600 | -99 | 94 | -1056 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1480 | 1587 | -107 | 93 | -1037 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1450 | 1587 | -137 | 91 | -1018 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1437 | 1587 | -150 | 91 | -1012 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1416 | 1587 | -171 | 89 | -996 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1416 | 1587 | -171 | 89 | -996 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1372 | 1587 | -215 | 86 | -945 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1371 | 1587 | -216 | 86 | -945 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1367 | 1587 | -220 | 86 | -968 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1361 | 1587 | -226 | 86 | -959 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1356 | 1587 | -231 | 85 | -960 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1345 | 1587 | -242 | 85 | -947 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1332 | 1600 | -268 | 83 | -891 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1330 | 1600 | -270 | 83 | -902 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1317 | 1600 | -283 | 82 | -872 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1297 | 1600 | -303 | 81 | -870 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1281 | 1587 | -306 | 81 | -903 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1290 | 1600 | -310 | 81 | -909 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1268 | 1587 | -319 | 80 | -895 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1587 | -321 | 80 | -892 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1255 | 1587 | -332 | 79 | -886 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1587 | -356 | 78 | -869 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1587 | -357 | 78 | -866 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1587 | -357 | 78 | -870 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1587 | -358 | 77 | -868 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1587 | -358 | 77 | -868 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1587 | -365 | 77 | -864 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1587 | -365 | 77 | -868 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1587 | -368 | 77 | -861 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -861 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -861 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -860 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -860 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -858 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -854 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1587 | -381 | 76 | -852 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1587 | -382 | 76 | -851 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1587 | -382 | 76 | -851 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1587 | -383 | 76 | -850 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1587 | -396 | 75 | -842 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1587 | -418 | 74 | -827 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1587 | -432 | 73 | -814 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1130 | 1587 | -457 | 71 | -795 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1587 | -461 | 71 | -797 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1117 | 1587 | -470 | 70 | -791 | AC

## 1430
Detailed results
Generated at: | 14/07/2026 21:21:35
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3534.31
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1593 | 1587 | 6 | 100 | -1120 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1504 | 1600 | -96 | 94 | -1057 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1488 | 1587 | -99 | 94 | -1042 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1458 | 1587 | -129 | 92 | -1025 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1453 | 1587 | -134 | 92 | -1019 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1421 | 1587 | -166 | 90 | -998 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1417 | 1587 | -170 | 89 | -996 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1381 | 1587 | -206 | 87 | -951 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1380 | 1587 | -207 | 87 | -951 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1377 | 1587 | -210 | 87 | -970 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1386 | 1600 | -214 | 87 | -924 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1369 | 1600 | -231 | 86 | -934 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1348 | 1587 | -239 | 85 | -949 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1342 | 1600 | -258 | 84 | -898 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1331 | 1587 | -256 | 84 | -942 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1319 | 1587 | -268 | 83 | -934 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1322 | 1600 | -278 | 83 | -907 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1279 | 1587 | -308 | 81 | -901 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1287 | 1600 | -313 | 80 | -907 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1263 | 1587 | -324 | 80 | -890 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1587 | -330 | 79 | -887 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1587 | -354 | 78 | -870 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1587 | -359 | 77 | -866 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1587 | -360 | 77 | -868 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1587 | -362 | 77 | -865 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1587 | -362 | 77 | -864 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1587 | -365 | 77 | -860 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1587 | -365 | 77 | -863 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -859 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -858 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1587 | -373 | 77 | -858 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1587 | -373 | 76 | -857 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -859 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -855 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1587 | -379 | 76 | -855 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1587 | -382 | 76 | -851 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -385 | 76 | -849 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1587 | -386 | 76 | -848 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1587 | -387 | 76 | -848 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1587 | -388 | 76 | -846 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1587 | -399 | 75 | -839 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1587 | -414 | 74 | -828 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1587 | -434 | 73 | -813 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1587 | -465 | 71 | -790 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1587 | -465 | 71 | -793 | AC

## 1530
Detailed results
Generated at: | 14/07/2026 21:21:35
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3685.68
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1592 | 1587 | 5 | 100 | -1119 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1514 | 1587 | -73 | 95 | -1058 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1516 | 1600 | -84 | 95 | -1065 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1500 | 1600 | -100 | 94 | -996 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1473 | 1587 | -114 | 93 | -1032 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1474 | 1600 | -126 | 92 | -1013 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1462 | 1587 | -125 | 92 | -1027 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1451 | 1600 | -149 | 91 | -969 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1438 | 1587 | -149 | 91 | -1009 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1433 | 1587 | -154 | 90 | -1007 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1411 | 1600 | -189 | 88 | -973 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1382 | 1587 | -205 | 87 | -972 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1382 | 1587 | -206 | 87 | -950 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1381 | 1587 | -206 | 87 | -951 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1354 | 1587 | -233 | 85 | -952 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1312 | 1587 | -275 | 83 | -928 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1300 | 1587 | -287 | 82 | -920 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1294 | 1600 | -306 | 81 | -911 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1282 | 1587 | -305 | 81 | -903 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1267 | 1587 | -320 | 80 | -891 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1253 | 1587 | -334 | 79 | -884 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1587 | -359 | 77 | -866 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1587 | -361 | 77 | -867 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1587 | -362 | 77 | -865 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1587 | -365 | 77 | -863 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1587 | -366 | 77 | -862 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1587 | -367 | 77 | -861 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1587 | -368 | 77 | -857 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1587 | -371 | 77 | -858 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -857 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -857 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1587 | -375 | 76 | -856 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1587 | -379 | 76 | -853 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1587 | -380 | 76 | -857 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1587 | -381 | 76 | -853 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1587 | -383 | 76 | -850 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -845 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -845 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1587 | -391 | 75 | -844 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -842 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1587 | -396 | 75 | -841 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1187 | 1600 | -413 | 74 | -803 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1186 | 1600 | -414 | 74 | -802 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1587 | -411 | 74 | -831 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1173 | 1600 | -427 | 73 | -795 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1162 | 1600 | -438 | 73 | -785 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1587 | -439 | 72 | -809 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1132 | 1600 | -468 | 71 | -766 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1132 | 1600 | -468 | 71 | -766 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1129 | 1600 | -471 | 71 | -766 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1120 | 1587 | -467 | 71 | -792 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1115 | 1587 | -472 | 70 | -784 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1121 | 1600 | -479 | 70 | -765 | AC

## 1630
Detailed results
Generated at: | 14/07/2026 21:21:35
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3453.71
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1591 | 1587 | 4 | 100 | -1119 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1497 | 1587 | -90 | 94 | -1048 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1493 | 1587 | -94 | 94 | -1049 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1492 | 1600 | -108 | 93 | -1049 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1416 | 1587 | -171 | 89 | -994 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1413 | 1587 | -174 | 89 | -994 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1411 | 1587 | -176 | 89 | -991 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1399 | 1587 | -188 | 88 | -983 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1382 | 1587 | -205 | 87 | -952 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1381 | 1587 | -206 | 87 | -952 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1382 | 1600 | -218 | 86 | -928 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1342 | 1587 | -245 | 85 | -944 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1275 | 1587 | -312 | 80 | -901 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1270 | 1587 | -317 | 80 | -895 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1273 | 1600 | -327 | 80 | -897 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1587 | -325 | 80 | -893 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1587 | -325 | 80 | -888 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1240 | 1587 | -347 | 78 | -874 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1587 | -349 | 78 | -873 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1246 | 1600 | -354 | 78 | -845 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1587 | -361 | 77 | -865 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1587 | -362 | 77 | -865 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1587 | -364 | 77 | -863 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -859 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -856 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -853 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -856 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -856 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -854 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -853 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1587 | -383 | 76 | -850 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1587 | -383 | 76 | -851 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1587 | -386 | 76 | -847 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1587 | -386 | 76 | -847 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1587 | -386 | 76 | -847 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1587 | -387 | 76 | -847 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1587 | -394 | 75 | -842 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1587 | -396 | 75 | -841 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1587 | -397 | 75 | -840 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1587 | -405 | 75 | -839 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1177 | 1600 | -423 | 74 | -817 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1587 | -425 | 73 | -819 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1139 | 1600 | -461 | 71 | -807 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1587 | -465 | 71 | -790 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1587 | -466 | 71 | -792 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1114 | 1587 | -473 | 70 | -787 | AC

## 1730
Detailed results
Generated at: | 14/07/2026 21:21:35
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3398.66
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1591 | 1587 | 4 | 100 | -1115 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1588 | 1587 | 1 | 100 | -1118 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1500 | 1587 | -87 | 95 | -1053 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1458 | 1587 | -129 | 92 | -1022 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1450 | 1600 | -150 | 91 | -1021 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1391 | 1587 | -196 | 88 | -959 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1390 | 1587 | -197 | 88 | -960 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1378 | 1587 | -209 | 87 | -969 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1356 | 1587 | -231 | 85 | -954 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1348 | 1587 | -239 | 85 | -949 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1323 | 1587 | -264 | 83 | -932 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1255 | 1587 | -332 | 79 | -886 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1248 | 1587 | -339 | 79 | -881 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1242 | 1587 | -345 | 78 | -875 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1251 | 1600 | -349 | 78 | -883 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1224 | 1600 | -376 | 76 | -829 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1587 | -373 | 76 | -857 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1587 | -375 | 76 | -856 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1587 | -376 | 76 | -855 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1587 | -382 | 76 | -851 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1587 | -382 | 76 | -851 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1587 | -386 | 76 | -848 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1587 | -386 | 76 | -848 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1587 | -386 | 76 | -848 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1587 | -388 | 76 | -847 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -846 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -842 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1587 | -396 | 75 | -842 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1587 | -396 | 75 | -841 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1587 | -396 | 75 | -838 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1587 | -397 | 75 | -841 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1587 | -397 | 75 | -840 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1587 | -403 | 75 | -838 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1587 | -405 | 75 | -835 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1587 | -411 | 74 | -831 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1587 | -413 | 74 | -830 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1587 | -437 | 72 | -816 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1146 | 1587 | -441 | 72 | -768 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1136 | 1587 | -451 | 72 | -806 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1130 | 1587 | -457 | 71 | -798 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1128 | 1587 | -459 | 71 | -797 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1127 | 1587 | -460 | 71 | -794 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1116 | 1587 | -471 | 70 | -793 | AC

## 1830
Detailed results
Generated at: | 14/07/2026 21:21:35
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3426.92
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1588 | 1587 | 1 | 100 | -1113 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1583 | 1587 | -4 | 100 | -1115 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1508 | 1587 | -79 | 95 | -1059 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1460 | 1587 | -127 | 92 | -1024 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1434 | 1600 | -166 | 90 | -1010 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1390 | 1587 | -197 | 88 | -959 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1389 | 1587 | -198 | 88 | -959 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1374 | 1587 | -213 | 87 | -967 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1355 | 1587 | -232 | 85 | -954 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1334 | 1587 | -253 | 84 | -940 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1311 | 1587 | -276 | 83 | -924 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1260 | 1587 | -327 | 79 | -889 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1587 | -341 | 78 | -879 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1241 | 1587 | -346 | 78 | -876 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1248 | 1600 | -352 | 78 | -881 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1587 | -350 | 78 | -872 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1234 | 1600 | -366 | 77 | -835 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1587 | -375 | 76 | -856 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1587 | -381 | 76 | -852 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1587 | -383 | 76 | -851 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1587 | -387 | 76 | -848 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1587 | -387 | 76 | -848 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1587 | -393 | 75 | -844 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1587 | -393 | 75 | -844 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1587 | -393 | 75 | -844 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -842 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1587 | -396 | 75 | -841 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1587 | -397 | 75 | -838 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1587 | -398 | 75 | -841 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1587 | -399 | 75 | -839 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1587 | -401 | 75 | -838 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1587 | -403 | 75 | -837 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1587 | -403 | 75 | -837 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1587 | -406 | 74 | -836 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1587 | -410 | 74 | -832 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1587 | -414 | 74 | -829 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1166 | 1587 | -420 | 74 | -780 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1587 | -424 | 73 | -822 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1587 | -426 | 73 | -821 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1136 | 1587 | -451 | 72 | -806 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1587 | -464 | 71 | -797 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1587 | -465 | 71 | -791 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1587 | -465 | 71 | -793 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1587 | -466 | 71 | -792 | AC

## 1930
Detailed results
Generated at: | 14/07/2026 21:21:35
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3724.67
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2/[GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1582 | 1587 | -5 | 100 | -1111 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1593 | 1600 | -7 | 100 | -1040 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1556 | 1587 | -31 | 98 | -1089 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1556 | 1587 | -31 | 98 | -1084 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1492 | 1587 | -95 | 94 | -1045 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1495 | 1600 | -105 | 93 | -1049 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1434 | 1587 | -153 | 90 | -1005 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1427 | 1587 | -160 | 90 | -1000 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1419 | 1587 | -168 | 89 | -995 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1394 | 1600 | -206 | 87 | -923 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1374 | 1587 | -213 | 87 | -943 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1373 | 1587 | -214 | 87 | -944 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1350 | 1587 | -237 | 85 | -948 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1346 | 1600 | -254 | 84 | -922 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1282 | 1587 | -305 | 81 | -902 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1285 | 1600 | -315 | 80 | -903 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1267 | 1587 | -320 | 80 | -891 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1587 | -323 | 80 | -889 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1258 | 1600 | -342 | 79 | -864 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1587 | -357 | 78 | -866 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1587 | -364 | 77 | -861 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -858 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -856 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1587 | -376 | 76 | -853 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -852 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1587 | -380 | 76 | -850 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1587 | -382 | 76 | -849 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1587 | -383 | 76 | -848 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1587 | -384 | 76 | -848 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -385 | 76 | -844 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -385 | 76 | -847 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1587 | -387 | 76 | -846 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1587 | -389 | 75 | -844 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -844 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1206 | 1600 | -394 | 75 | -806 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1206 | 1600 | -394 | 75 | -806 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1587 | -392 | 75 | -842 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1587 | -394 | 75 | -843 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1587 | -394 | 75 | -841 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1587 | -404 | 75 | -834 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1191 | 1600 | -409 | 74 | -797 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1189 | 1600 | -411 | 74 | -793 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1587 | -422 | 73 | -821 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1170 | 1600 | -430 | 73 | -782 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1587 | -434 | 73 | -813 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1587 | -444 | 72 | -808 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1147 | 1600 | -453 | 72 | -768 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1144 | 1600 | -456 | 72 | -765 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1587 | -454 | 71 | -798 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1141 | 1600 | -459 | 71 | -764 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1130 | 1587 | -457 | 71 | -800 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1128 | 1587 | -459 | 71 | -799 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1122 | 1587 | -465 | 71 | -766 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1587 | -466 | 71 | -791 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1123 | 1600 | -477 | 70 | -751 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1111 | 1587 | -476 | 70 | -781 | AC

## 2030
Detailed results
Generated at: | 14/07/2026 21:21:36
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3539.52
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2/[GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1601 | 1600 | 1 | 100 | -1034 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1482 | 1587 | -105 | 93 | -1033 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1472 | 1587 | -115 | 93 | -1034 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1446 | 1587 | -141 | 91 | -1013 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1405 | 1600 | -195 | 88 | -986 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1392 | 1587 | -195 | 88 | -976 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1384 | 1600 | -216 | 86 | -906 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1351 | 1587 | -236 | 85 | -947 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1348 | 1587 | -239 | 85 | -945 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1342 | 1587 | -245 | 85 | -940 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1326 | 1600 | -274 | 83 | -905 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1269 | 1587 | -318 | 80 | -891 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1269 | 1587 | -318 | 80 | -872 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1269 | 1587 | -318 | 80 | -873 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1223 | 1600 | -377 | 76 | -844 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1587 | -386 | 76 | -845 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | -847 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1200 | 1600 | -400 | 75 | -789 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1587 | -400 | 75 | -835 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1587 | -401 | 75 | -833 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1193 | 1600 | -407 | 75 | -787 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1192 | 1600 | -408 | 74 | -787 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1191 | 1600 | -409 | 74 | -786 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1587 | -435 | 73 | -811 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1155 | 1600 | -445 | 72 | -762 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1587 | -442 | 72 | -806 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1137 | 1587 | -450 | 72 | -800 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1137 | 1587 | -450 | 72 | -802 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1134 | 1587 | -453 | 71 | -798 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1143 | 1600 | -457 | 71 | -753 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1587 | -455 | 71 | -797 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1129 | 1587 | -458 | 71 | -795 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1587 | -461 | 71 | -793 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1587 | -461 | 71 | -793 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1587 | -461 | 71 | -793 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1135 | 1600 | -465 | 71 | -749 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1587 | -461 | 71 | -790 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1125 | 1587 | -462 | 71 | -793 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1133 | 1600 | -467 | 71 | -747 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1587 | -464 | 71 | -791 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1130 | 1600 | -470 | 71 | -746 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1587 | -466 | 71 | -789 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1119 | 1587 | -468 | 71 | -788 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1118 | 1587 | -469 | 70 | -787 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1118 | 1587 | -469 | 70 | -787 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1116 | 1587 | -471 | 70 | -788 | AC

## 2130
Detailed results
Generated at: | 14/07/2026 21:21:36
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3584.69
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2/[GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1591 | 1600 | -9 | 99 | -1036 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1511 | 1587 | -76 | 95 | -1049 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1485 | 1587 | -102 | 94 | -1044 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1457 | 1587 | -130 | 92 | -1020 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1438 | 1600 | -162 | 90 | -1007 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1397 | 1587 | -190 | 88 | -980 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1376 | 1587 | -211 | 87 | -967 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1375 | 1587 | -212 | 87 | -964 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1383 | 1600 | -217 | 86 | -919 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1362 | 1587 | -225 | 86 | -956 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1355 | 1600 | -245 | 85 | -930 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1333 | 1600 | -267 | 83 | -918 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1280 | 1587 | -307 | 81 | -901 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1268 | 1587 | -319 | 80 | -872 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1268 | 1587 | -319 | 80 | -872 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1587 | -375 | 76 | -854 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1587 | -376 | 76 | -854 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1587 | -380 | 76 | -849 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1600 | -384 | 76 | -857 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1587 | -424 | 73 | -820 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1587 | -426 | 73 | -819 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1154 | 1587 | -433 | 73 | -814 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1587 | -434 | 73 | -816 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1156 | 1600 | -444 | 72 | -777 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1587 | -441 | 72 | -807 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1156 | 1600 | -444 | 72 | -776 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1587 | -441 | 72 | -809 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1587 | -441 | 72 | -809 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1587 | -441 | 72 | -809 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1155 | 1600 | -445 | 72 | -775 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1587 | -443 | 72 | -808 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1587 | -444 | 72 | -808 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1142 | 1587 | -445 | 72 | -807 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1142 | 1587 | -445 | 72 | -807 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1141 | 1587 | -446 | 72 | -806 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1141 | 1587 | -446 | 72 | -805 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1137 | 1587 | -450 | 72 | -804 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1136 | 1587 | -451 | 72 | -802 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1587 | -452 | 72 | -801 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1144 | 1600 | -456 | 71 | -770 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1129 | 1587 | -458 | 71 | -798 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1120 | 1587 | -467 | 71 | -791 | AC

## 2230
Detailed results
Generated at: | 14/07/2026 21:21:36
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3723.36
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1593 | 1587 | 6 | 100 | -1118 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1576 | 1587 | -11 | 99 | -1092 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1572 | 1587 | -15 | 99 | -1098 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1543 | 1600 | -57 | 96 | -1009 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1514 | 1600 | -86 | 95 | -1058 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1501 | 1587 | -86 | 95 | -1050 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1452 | 1587 | -135 | 91 | -1016 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1446 | 1587 | -141 | 91 | -1015 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1432 | 1587 | -155 | 90 | -1004 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1372 | 1587 | -215 | 86 | -942 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1372 | 1587 | -215 | 86 | -941 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1354 | 1587 | -233 | 85 | -952 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1358 | 1600 | -242 | 85 | -904 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1347 | 1600 | -253 | 84 | -920 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1344 | 1600 | -256 | 84 | -918 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1289 | 1587 | -298 | 81 | -907 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1288 | 1587 | -299 | 81 | -908 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1280 | 1587 | -307 | 81 | -899 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1288 | 1600 | -312 | 81 | -907 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1587 | -350 | 78 | -871 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1587 | -354 | 78 | -870 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1587 | -359 | 77 | -868 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1587 | -361 | 77 | -866 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1587 | -367 | 77 | -861 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1587 | -367 | 77 | -861 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1587 | -368 | 77 | -861 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1587 | -368 | 77 | -861 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1587 | -368 | 77 | -858 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -860 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1587 | -371 | 77 | -859 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1587 | -371 | 77 | -859 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -858 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1587 | -373 | 77 | -857 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1587 | -376 | 76 | -855 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1587 | -377 | 76 | -856 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1587 | -380 | 76 | -853 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1587 | -388 | 76 | -847 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1587 | -388 | 76 | -847 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1587 | -406 | 74 | -836 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1587 | -406 | 74 | -834 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1168 | 1587 | -419 | 74 | -828 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1587 | -423 | 73 | -822 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1587 | -426 | 73 | -820 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1587 | -430 | 73 | -819 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1587 | -439 | 72 | -814 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1143 | 1600 | -457 | 71 | -769 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1143 | 1600 | -457 | 71 | -769 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1139 | 1600 | -461 | 71 | -765 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1125 | 1587 | -462 | 71 | -792 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1123 | 1587 | -464 | 71 | -761 | AC

## 2330
Detailed results
Generated at: | 14/07/2026 21:21:36
Business day: | 2026-07-16
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3330.94
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1593 | 1587 | 6 | 100 | -1114 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1580 | 1587 | -7 | 100 | -1112 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1512 | 1587 | -75 | 95 | -1060 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1458 | 1587 | -129 | 92 | -1019 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1454 | 1600 | -146 | 91 | -1020 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1382 | 1587 | -205 | 87 | -973 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1382 | 1587 | -205 | 87 | -953 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1382 | 1587 | -205 | 87 | -952 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1371 | 1587 | -216 | 86 | -966 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1343 | 1587 | -244 | 85 | -945 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1319 | 1587 | -268 | 83 | -930 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1273 | 1587 | -314 | 80 | -899 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1242 | 1587 | -345 | 78 | -876 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1587 | -348 | 78 | -876 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1248 | 1600 | -352 | 78 | -838 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | -880 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1587 | -366 | 77 | -863 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1587 | -378 | 76 | -855 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1587 | -380 | 76 | -855 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1587 | -385 | 76 | -851 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1587 | -389 | 76 | -848 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -847 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -847 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1587 | -391 | 75 | -847 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1587 | -391 | 75 | -847 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -844 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -844 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1587 | -397 | 75 | -843 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1587 | -398 | 75 | -842 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1587 | -398 | 75 | -842 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1587 | -401 | 75 | -836 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1587 | -402 | 75 | -839 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1587 | -406 | 74 | -836 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1587 | -407 | 74 | -835 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1587 | -407 | 74 | -837 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1587 | -408 | 74 | -835 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1587 | -420 | 74 | -826 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1136 | 1587 | -451 | 72 | -759 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1587 | -464 | 71 | -793 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1117 | 1587 | -470 | 70 | -792 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1112 | 1587 | -475 | 70 | -788 | AC