## 0030
Detailed results
Generated at: | 23/07/2026 23:35:13
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3124
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00001 | GR | GPKOMO31_generator | 0 | 172 |  |  | 142 | 0 |  | 172 | 0 | FALSE | TRUE
GR_RA_00002 | GR | GPKOMO33_generator | 0 | 336 |  |  | 73 | 0 |  | 336 | 0 | FALSE | TRUE
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 488 | 0 |  | 902 | 0 | FALSE | TRUE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 230 | 0 |  | 421 | 0 | FALSE | TRUE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 347 | 663 |  | 663 | 0 | FALSE | FALSE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 0 | 205 |  | 340 | 0 | TRUE | FALSE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 236 | 109 |  | 451 | 0 | FALSE | FALSE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 264 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 243 | 450 |  | 450 | 0 | FALSE | FALSE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 213 | 419 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 301 | 536 |  | 536 | 0 | FALSE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 181 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 69 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 89 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1582 | 1587 | -5 | 100 | 1135 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1445 | 1587 | -142 | 91 | 1038 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1342 | 1587 | -245 | 85 | 961 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1338 | 1587 | -249 | 84 | -948 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1311 | 1587 | -276 | 83 | 938 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1300 | 1600 | -300 | 81 | -878 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1298 | 1600 | -302 | 81 | -875 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1281 | 1587 | -306 | 81 | 906 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1281 | 1587 | -306 | 81 | 917 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1280 | 1587 | -308 | 81 | 903 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1247 | 1587 | -340 | 79 | 860 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1237 | 1587 | -350 | 78 | -860 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1237 | 1587 | -350 | 78 | -861 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1229 | 1587 | -358 | 77 | 881 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1219 | 1587 | -368 | 77 | 873 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1217 | 1587 | -370 | 77 | 871 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1214 | 1587 | -373 | 76 | 869 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1212 | 1587 | -375 | 76 | 866 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1212 | 1587 | -375 | 76 | 868 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1209 | 1587 | -378 | 76 | 865 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1208 | 1587 | -379 | 76 | 863 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1208 | 1587 | -379 | 76 | 864 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1208 | 1587 | -379 | 76 | 864 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1207 | 1587 | -380 | 76 | 864 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1207 | 1587 | -380 | 76 | 865 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1207 | 1587 | -380 | 76 | 864 | AC
Base case | Base case | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1207 | 1587 | -380 | 76 | 864 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1207 | 1587 | -380 | 76 | 864 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1207 | 1587 | -380 | 76 | 864 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1207 | 1587 | -380 | 76 | 864 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1206 | 1587 | -381 | 76 | 864 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1206 | 1587 | -381 | 76 | 864 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1206 | 1587 | -381 | 76 | 864 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1206 | 1587 | -381 | 76 | 864 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1206 | 1587 | -381 | 76 | 864 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1206 | 1587 | -381 | 76 | 864 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1206 | 1587 | -381 | 76 | 864 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1205 | 1587 | -382 | 76 | 862 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1205 | 1587 | -382 | 76 | 863 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1204 | 1587 | -383 | 76 | 861 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1204 | 1587 | -383 | 76 | 862 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1203 | 1587 | -384 | 76 | 862 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1197 | 1587 | -390 | 75 | 857 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1195 | 1587 | -392 | 75 | 856 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1194 | 1587 | -393 | 75 | 855 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1192 | 1587 | -395 | 75 | 853 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1192 | 1587 | -395 | 75 | 853 | AC
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1181 | 1587 | -406 | 74 | 845 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1180 | 1587 | -407 | 74 | 843 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1587 | -409 | 74 | -832 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1587 | -414 | 74 | -830 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1587 | -420 | 74 | -826 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1587 | -425 | 73 | -823 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1156 | 1600 | -444 | 72 | -795 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1144 | 1587 | -443 | 72 | 809 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1142 | 1587 | -445 | 72 | 806 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | -812 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1135 | 1587 | -452 | 72 | 816 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1140 | 1600 | -460 | 71 | -767 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1129 | 1587 | -458 | 71 | 804 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1112 | 1587 | -475 | 70 | -788 | AC

## 0130
Detailed results
Generated at: | 23/07/2026 23:35:13
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3375
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00001 | GR | GPKOMO31_generator | 0 | 172 |  |  | 37 | 0 |  | 172 | 0 | FALSE | TRUE
GR_RA_00002 | GR | GPKOMO33_generator | 0 | 336 |  |  | 19 | 0 |  | 336 | 0 | FALSE | TRUE
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 506 | 0 |  | 902 | 0 | FALSE | TRUE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 238 | 0 |  | 421 | 0 | FALSE | TRUE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 316 | 575 |  | 663 | 0 | FALSE | FALSE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 0 | 168 |  | 168 | 0 | TRUE | FALSE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 243 | 272 |  | 451 | 0 | FALSE | FALSE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 272 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 250 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 219 | 419 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 139 | 536 |  | 536 | 0 | FALSE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 188 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 16 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 21 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1582 | 1587 | -5 | 100 | 1132 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1453 | 1587 | -134 | 92 | -1028 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1416 | 1587 | -171 | 89 | 1014 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1402 | 1587 | -185 | 88 | 990 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1409 | 1600 | -191 | 88 | -944 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1406 | 1600 | -194 | 88 | -941 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1338 | 1587 | -249 | 84 | -927 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1337 | 1587 | -250 | 84 | -927 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1321 | 1587 | -266 | 83 | 942 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1321 | 1587 | -266 | 83 | 908 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1284 | 1587 | -303 | 81 | 915 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1282 | 1587 | -305 | 81 | -905 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1281 | 1587 | -306 | 81 | -906 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1277 | 1587 | -310 | 80 | -902 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1274 | 1587 | -313 | 80 | -900 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1600 | -343 | 79 | -889 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1245 | 1587 | -342 | 78 | 888 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1235 | 1587 | -352 | 78 | 872 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1587 | -366 | 77 | -865 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1228 | 1600 | -372 | 77 | -842 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1587 | -390 | 75 | -848 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1205 | 1600 | -395 | 75 | -808 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1196 | 1587 | -392 | 75 | 854 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1177 | 1587 | -410 | 74 | 840 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1186 | 1600 | -414 | 74 | -804 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1172 | 1587 | -415 | 74 | 836 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1172 | 1587 | -415 | 74 | 836 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1171 | 1587 | -416 | 74 | 834 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1169 | 1587 | -418 | 74 | 824 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1168 | 1587 | -419 | 74 | 832 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1167 | 1587 | -420 | 74 | 831 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1167 | 1587 | -420 | 74 | 830 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1166 | 1587 | -421 | 73 | 831 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1166 | 1587 | -421 | 73 | 831 | AC
Base case | Base case | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1166 | 1587 | -422 | 73 | 831 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1165 | 1587 | -422 | 73 | 831 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1165 | 1587 | -422 | 73 | 831 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1165 | 1587 | -422 | 73 | 831 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1165 | 1587 | -422 | 73 | 831 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1165 | 1587 | -422 | 73 | 831 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1165 | 1587 | -422 | 73 | 831 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1165 | 1587 | -422 | 73 | 831 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1587 | -422 | 73 | -826 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1165 | 1587 | -422 | 73 | 831 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1165 | 1587 | -422 | 73 | 831 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1165 | 1587 | -422 | 73 | 831 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1164 | 1587 | -423 | 73 | 830 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1164 | 1587 | -423 | 73 | 829 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1162 | 1587 | -425 | 73 | 829 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1161 | 1587 | -426 | 73 | 828 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1160 | 1587 | -427 | 73 | 828 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1160 | 1587 | -427 | 73 | 826 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1159 | 1587 | -428 | 73 | 826 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1159 | 1587 | -428 | 73 | 825 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1152 | 1587 | -435 | 73 | 821 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1149 | 1587 | -438 | 72 | 819 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1149 | 1587 | -438 | 72 | 819 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1148 | 1587 | -439 | 72 | 819 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1148 | 1587 | -439 | 72 | 819 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1155 | 1600 | -445 | 72 | -783 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1155 | 1600 | -445 | 72 | -783 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1146 | 1600 | -454 | 72 | -776 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1134 | 1587 | -453 | 71 | 807 | AC
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1133 | 1587 | -454 | 71 | 807 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1131 | 1587 | -456 | 71 | 800 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1135 | 1600 | -465 | 71 | -770 | AC

## 0230
Detailed results
Generated at: | 23/07/2026 23:35:13
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 2933
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 501 | 0 |  | 902 | 0 | FALSE | TRUE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 236 | 0 |  | 421 | 0 | FALSE | TRUE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 313 | 437 |  | 663 | 0 | FALSE | FALSE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 0 | 168 |  | 168 | 0 | TRUE | FALSE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 242 | 160 |  | 451 | 0 | FALSE | FALSE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 269 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 248 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 217 | 419 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 536 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 186 | 0 |  | 314 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1584 | 1587 | -4 | 100 | 1128 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1577 | 1587 | -10 | 99 | -1112 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1511 | 1600 | -89 | 94 | -1007 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1509 | 1600 | -91 | 94 | -1003 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1477 | 1587 | -110 | 93 | 1037 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1447 | 1587 | -140 | 91 | -997 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1447 | 1587 | -140 | 91 | -996 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1412 | 1587 | -175 | 89 | -994 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1391 | 1587 | -196 | 88 | -978 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1389 | 1587 | -198 | 88 | -978 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1387 | 1587 | -200 | 87 | 990 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1385 | 1587 | -202 | 87 | -976 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1372 | 1587 | -215 | 86 | 941 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1376 | 1600 | -224 | 86 | -969 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1343 | 1587 | -244 | 85 | -947 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1306 | 1587 | -281 | 82 | -922 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1302 | 1587 | -285 | 82 | 925 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1300 | 1600 | -300 | 81 | -888 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1288 | 1587 | -299 | 81 | -911 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1292 | 1600 | -308 | 81 | -871 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1278 | 1587 | -309 | 81 | 900 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1258 | 1587 | -329 | 79 | 894 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1248 | 1587 | -339 | 79 | 872 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1257 | 1600 | -343 | 79 | -837 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1253 | 1600 | -347 | 78 | -844 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1252 | 1600 | -348 | 78 | -844 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1237 | 1600 | -363 | 77 | -835 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1225 | 1600 | -375 | 77 | -828 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1208 | 1587 | -379 | 76 | 858 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | -860 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1587 | -388 | 76 | -849 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1587 | -392 | 75 | -847 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1195 | 1600 | -405 | 75 | -808 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1185 | 1587 | -402 | 75 | 834 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1587 | -405 | 74 | -836 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1186 | 1600 | -414 | 74 | -802 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1587 | -418 | 74 | -829 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1159 | 1587 | -428 | 73 | -804 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1158 | 1587 | -429 | 73 | 825 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1587 | -429 | 73 | -821 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1587 | -429 | 73 | -821 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1166 | 1600 | -434 | 73 | -790 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1587 | -434 | 73 | -818 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1587 | -435 | 73 | -817 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1154 | 1600 | -446 | 72 | -781 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1587 | -444 | 72 | -811 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1587 | -444 | 72 | -811 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1141 | 1587 | -446 | 72 | 735 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1150 | 1600 | -450 | 72 | -779 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1587 | -447 | 72 | -809 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1587 | -447 | 72 | -809 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1587 | -447 | 72 | -809 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1140 | 1587 | -447 | 72 | 804 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1136 | 1587 | -451 | 72 | -806 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1587 | -452 | 72 | -806 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1135 | 1587 | -452 | 72 | 808 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1134 | 1587 | -452 | 71 | -805 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1587 | -454 | 71 | -804 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1587 | -454 | 71 | -804 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1131 | 1587 | -456 | 71 | 805 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1130 | 1587 | -457 | 71 | -779 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1129 | 1587 | -458 | 71 | 803 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1129 | 1587 | -458 | 71 | 801 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1127 | 1587 | -460 | 71 | -800 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1126 | 1587 | -461 | 71 | -775 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1125 | 1587 | -462 | 71 | 800 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1125 | 1587 | -462 | 71 | -776 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1124 | 1587 | -463 | 71 | 798 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1124 | 1587 | -463 | 71 | 797 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1124 | 1587 | -463 | 71 | 799 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1124 | 1587 | -464 | 71 | 799 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1587 | -464 | 71 | -797 | AC
Base case | Base case | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1123 | 1587 | -464 | 71 | 799 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1123 | 1587 | -464 | 71 | 799 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1123 | 1587 | -464 | 71 | 799 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1123 | 1587 | -464 | 71 | 799 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1123 | 1587 | -464 | 71 | 799 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1123 | 1587 | -464 | 71 | 799 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1123 | 1587 | -464 | 71 | 799 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1123 | 1587 | -464 | 71 | 799 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1122 | 1587 | -465 | 71 | 799 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1122 | 1587 | -465 | 71 | 799 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1122 | 1587 | -465 | 71 | 799 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1587 | -465 | 71 | -797 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1121 | 1587 | -466 | 71 | 798 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1121 | 1587 | -466 | 71 | 797 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1587 | -466 | 71 | -795 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1120 | 1587 | -467 | 71 | 796 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1120 | 1587 | -467 | 71 | 797 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1117 | 1587 | -470 | 70 | 795 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1117 | 1587 | -470 | 70 | 795 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1117 | 1587 | -470 | 70 | -790 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1124 | 1600 | -476 | 70 | -762 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1114 | 1587 | -473 | 70 | 792 | AC

## 0330
Detailed results
Generated at: | 23/07/2026 23:35:13
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3379
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 524 | 5 |  | 902 | 0 | FALSE | FALSE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 246 | 0 |  | 421 | 0 | FALSE | TRUE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 326 | 663 |  | 663 | 0 | FALSE | FALSE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 0 | 23 |  | 340 | 0 | TRUE | FALSE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 252 | 165 |  | 451 | 0 | FALSE | FALSE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 280 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 258 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 226 | 419 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 536 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 194 | 0 |  | 314 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1582 | 1587 | -5 | 100 | 1136 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1421 | 1587 | -166 | 90 | 1021 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1430 | 1600 | -170 | 89 | -959 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1430 | 1600 | -170 | 89 | -957 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1415 | 1587 | -172 | 89 | -1005 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1331 | 1587 | -256 | 84 | 953 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1311 | 1587 | -276 | 83 | -912 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1310 | 1587 | -277 | 83 | -912 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1293 | 1587 | -294 | 81 | 925 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1282 | 1587 | -305 | 81 | 906 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1280 | 1587 | -307 | 81 | 903 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1269 | 1587 | -318 | 80 | 875 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1587 | -330 | 79 | -889 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1255 | 1587 | -332 | 79 | 898 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1250 | 1587 | -337 | 79 | -886 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1248 | 1587 | -339 | 79 | -885 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1244 | 1587 | -343 | 78 | -881 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1242 | 1600 | -358 | 78 | -854 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1231 | 1600 | -369 | 77 | -831 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | -865 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1206 | 1587 | -381 | 76 | 865 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1208 | 1600 | -392 | 76 | -820 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1187 | 1587 | -400 | 75 | 851 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1587 | -400 | 75 | -843 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1183 | 1587 | -404 | 75 | 847 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1182 | 1587 | -405 | 74 | 846 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1182 | 1587 | -405 | 74 | 845 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1178 | 1587 | -409 | 74 | 843 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1178 | 1587 | -409 | 74 | 841 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1177 | 1587 | -410 | 74 | 842 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1177 | 1587 | -410 | 74 | 842 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1177 | 1587 | -410 | 74 | 842 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1176 | 1587 | -411 | 74 | 842 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1176 | 1587 | -411 | 74 | 842 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1176 | 1587 | -411 | 74 | 842 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1176 | 1587 | -411 | 74 | 842 | AC
Base case | Base case | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1176 | 1587 | -411 | 74 | 842 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1175 | 1587 | -412 | 74 | 842 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1175 | 1587 | -412 | 74 | 842 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1175 | 1587 | -412 | 74 | 842 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1175 | 1587 | -412 | 74 | 842 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1175 | 1587 | -412 | 74 | 842 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1175 | 1587 | -412 | 74 | 841 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1174 | 1587 | -413 | 74 | 840 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1173 | 1587 | -414 | 74 | 841 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1172 | 1587 | -415 | 74 | 840 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1172 | 1587 | -415 | 74 | 838 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1170 | 1587 | -417 | 74 | 838 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1170 | 1587 | -417 | 74 | 838 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1168 | 1587 | -419 | 74 | 836 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1168 | 1587 | -419 | 74 | -829 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1162 | 1587 | -425 | 73 | 831 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1161 | 1587 | -426 | 73 | 832 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1159 | 1587 | -428 | 73 | 830 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1157 | 1587 | -430 | 73 | 828 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1155 | 1587 | -432 | 73 | 827 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1161 | 1600 | -439 | 73 | -787 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1161 | 1600 | -439 | 73 | -786 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1160 | 1600 | -440 | 73 | -787 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1151 | 1587 | -436 | 73 | 824 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1143 | 1587 | -444 | 72 | 816 | AC
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1141 | 1587 | -446 | 72 | 816 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1144 | 1600 | -456 | 72 | -777 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1587 | -454 | 71 | -806 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1119 | 1587 | -468 | 71 | 791 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1117 | 1587 | -470 | 70 | 789 | AC

## 0430
Detailed results
Generated at: | 23/07/2026 23:35:13
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3325
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 531 | 5 |  | 902 | 0 | FALSE | FALSE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 248 | 0 |  | 421 | 0 | FALSE | TRUE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 328 | 663 |  | 663 | 0 | FALSE | FALSE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 0 | 17 |  | 340 | 0 | TRUE | FALSE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 254 | 0 |  | 451 | 0 | FALSE | TRUE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 278 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 259 | 450 |  | 450 | 0 | FALSE | FALSE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 228 | 157 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 536 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 195 | 0 |  | 314 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1582 | 1587 | -5 | 100 | 1135 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1453 | 1600 | -147 | 91 | -972 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1453 | 1600 | -147 | 91 | -974 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1422 | 1587 | -165 | 90 | 1022 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1380 | 1587 | -207 | 87 | -981 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1306 | 1587 | -281 | 82 | 935 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1280 | 1587 | -307 | 81 | 906 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1279 | 1587 | -308 | 81 | 903 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1276 | 1587 | -311 | 80 | -888 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1276 | 1587 | -311 | 80 | -888 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1274 | 1587 | -313 | 80 | 911 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1271 | 1587 | -316 | 80 | 876 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1279 | 1600 | -321 | 80 | -879 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1265 | 1600 | -335 | 79 | -846 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1250 | 1587 | -337 | 79 | 894 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1587 | -348 | 78 | -877 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1587 | -356 | 78 | -873 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1587 | -364 | 77 | -867 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1223 | 1600 | -377 | 76 | -829 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1201 | 1587 | -386 | 76 | 861 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1587 | -396 | 75 | -846 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | -850 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1187 | 1587 | -400 | 75 | 850 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1181 | 1587 | -406 | 74 | 845 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1180 | 1587 | -407 | 74 | 844 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1178 | 1587 | -409 | 74 | 842 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1175 | 1587 | -412 | 74 | 840 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1175 | 1587 | -412 | 74 | 838 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1174 | 1587 | -413 | 74 | 839 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1174 | 1587 | -413 | 74 | 840 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1174 | 1587 | -413 | 74 | 840 | AC
Base case | Base case | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1173 | 1587 | -414 | 74 | 840 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1173 | 1587 | -414 | 74 | 840 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1173 | 1587 | -414 | 74 | 840 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1173 | 1587 | -414 | 74 | 840 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1173 | 1587 | -414 | 74 | 839 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1173 | 1587 | -414 | 74 | 839 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1173 | 1587 | -414 | 74 | 839 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1173 | 1587 | -414 | 74 | 839 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1172 | 1587 | -415 | 74 | 839 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1182 | 1600 | -418 | 74 | -801 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1172 | 1587 | -415 | 74 | 839 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1172 | 1587 | -415 | 74 | 839 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1171 | 1587 | -416 | 74 | 838 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1171 | 1587 | -416 | 74 | 837 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1170 | 1587 | -417 | 74 | 837 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1168 | 1587 | -419 | 74 | 836 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1168 | 1587 | -419 | 74 | 836 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1168 | 1587 | -419 | 74 | 835 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1166 | 1587 | -421 | 73 | 834 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1166 | 1587 | -421 | 73 | 834 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1169 | 1600 | -431 | 73 | -793 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1168 | 1600 | -432 | 73 | -793 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1158 | 1587 | -429 | 73 | 829 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1158 | 1587 | -429 | 73 | 829 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1156 | 1587 | -431 | 73 | 827 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1155 | 1587 | -432 | 73 | 827 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1155 | 1587 | -432 | 73 | 827 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1587 | -442 | 72 | -813 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1152 | 1600 | -448 | 72 | -782 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1139 | 1587 | -448 | 72 | 814 | AC
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1139 | 1587 | -448 | 72 | 813 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1138 | 1587 | -449 | 72 | -810 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1133 | 1600 | -467 | 71 | -770 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1119 | 1587 | -468 | 70 | 792 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1117 | 1587 | -470 | 70 | 790 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1115 | 1587 | -472 | 70 | -794 | AC

## 0530
Detailed results
Generated at: | 23/07/2026 23:35:13
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 2832
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 565 | 0 |  | 902 | 0 | FALSE | TRUE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 262 | 348 |  | 421 | 0 | FALSE | FALSE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 347 | 591 |  | 663 | 0 | FALSE | FALSE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 0 | 2 |  | 168 | 0 | TRUE | FALSE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 269 | 0 |  | 451 | 0 | FALSE | TRUE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 298 | 41 |  | 838 | 0 | FALSE | FALSE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 275 | 450 |  | 450 | 0 | FALSE | FALSE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 241 | 0 |  | 419 | 0 | FALSE | TRUE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 536 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 206 | 0 |  | 314 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1586 | 1587 | -1 | 100 | 1138 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1345 | 1600 | -255 | 84 | -905 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1341 | 1600 | -259 | 84 | -902 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1330 | 1587 | -257 | 84 | 957 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1325 | 1587 | -262 | 83 | 936 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1322 | 1587 | -265 | 83 | 935 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1319 | 1587 | -268 | 83 | 915 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1255 | 1600 | -345 | 78 | -861 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1233 | 1600 | -367 | 77 | -809 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1183 | 1587 | -404 | 75 | 849 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1171 | 1587 | -416 | 74 | 839 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1164 | 1587 | -423 | 73 | 834 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1587 | -447 | 72 | -813 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1135 | 1587 | -452 | 72 | 814 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1132 | 1587 | -455 | 71 | 812 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1130 | 1587 | -457 | 71 | 812 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1124 | 1587 | -463 | 71 | 806 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1123 | 1587 | -464 | 71 | 807 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1123 | 1587 | -464 | 71 | 805 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1119 | 1587 | -468 | 70 | 802 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1116 | 1587 | -471 | 70 | 800 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1115 | 1587 | -472 | 70 | 800 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1115 | 1587 | -472 | 70 | 799 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1115 | 1587 | -472 | 70 | 800 | AC
Base case | Base case | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1115 | 1587 | -472 | 70 | 800 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1115 | 1587 | -472 | 70 | 800 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1115 | 1587 | -472 | 70 | 800 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1115 | 1587 | -472 | 70 | 800 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1115 | 1587 | -472 | 70 | 800 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1114 | 1587 | -473 | 70 | 800 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1114 | 1587 | -473 | 70 | 800 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1114 | 1587 | -473 | 70 | 799 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1114 | 1587 | -473 | 70 | 799 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1114 | 1587 | -473 | 70 | 799 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1114 | 1587 | -473 | 70 | 799 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1114 | 1587 | -473 | 70 | 799 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1114 | 1587 | -473 | 70 | 799 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1113 | 1587 | -474 | 70 | 799 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1113 | 1587 | -474 | 70 | 797 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1113 | 1587 | -474 | 70 | 798 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1112 | 1587 | -475 | 70 | 797 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1111 | 1587 | -476 | 70 | 797 | AC

## 0630
Detailed results
Generated at: | 23/07/2026 23:35:13
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 2144
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2/[GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 591 | 298 |  | 902 | 0 | FALSE | FALSE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 271 | 0 |  | 421 | 0 | FALSE | TRUE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 393 | 0 |  | 663 | 0 | FALSE | TRUE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 1 | 53 |  | 168 | 0 | FALSE | FALSE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 1 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 1 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 282 | 451 |  | 451 | 0 | FALSE | FALSE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 312 | 838 |  | 838 | 0 | FALSE | FALSE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 288 | 450 |  | 450 | 0 | FALSE | FALSE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 245 | 419 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 279 |  | 494 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 215 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 81 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 106 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1598 | 1600 | -2 | 100 | -1053 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1455 | 1600 | -145 | 91 | -968 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1377 | 1600 | -223 | 86 | -921 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1246 | 1600 | -354 | 78 | -854 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1237 | 1600 | -363 | 77 | -836 | AC
BG_CO_00001 | N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [BG-MK] [OPP] TIE 400 kV CHERVENA MOGILA - STIP | XCM_ST11 VCMOGL11 1 | 1393 | 1890 | -497 | 74 | 972 | AC
BG_MK_CO_00001 | N-1 TIE 400 kV CHERVENA MOGILA - STIP | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1377 | 1890 | -513 | 73 | 950 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1139 | 1600 | -461 | 71 | -770 | AC

## 0730
Detailed results
Generated at: | 23/07/2026 23:35:13
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 1871
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2/[GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 606 | 268 |  | 902 | 0 | FALSE | FALSE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 278 | 0 |  | 421 | 0 | FALSE | TRUE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 374 | 0 |  | 663 | 0 | FALSE | TRUE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 9 | 0 |  | 168 | 0 | FALSE | TRUE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 18 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 18 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 289 | 451 |  | 451 | 0 | FALSE | FALSE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 299 | 838 |  | 838 | 0 | FALSE | FALSE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 296 | 450 |  | 450 | 0 | FALSE | FALSE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 187 | 419 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 383 |  | 494 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 209 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 98 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 127 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1596 | 1600 | -4 | 100 | -1056 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1468 | 1600 | -132 | 92 | -980 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1373 | 1600 | -227 | 86 | -924 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1350 | 1600 | -250 | 84 | -890 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1348 | 1600 | -252 | 84 | -923 | AC
BG_CO_00001 | N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [BG-MK] [OPP] TIE 400 kV CHERVENA MOGILA - STIP | XCM_ST11 VCMOGL11 1 | 1436 | 1890 | -454 | 76 | 1008 | AC
BG_MK_CO_00001 | N-1 TIE 400 kV CHERVENA MOGILA - STIP | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1373 | 1890 | -517 | 73 | 953 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1142 | 1600 | -458 | 71 | -739 | AC

## 0830
Detailed results
Generated at: | 23/07/2026 23:35:14
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 1186
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2/[GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 570 | 437 |  | 902 | 0 | FALSE | FALSE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 263 | 421 |  | 421 | 0 | FALSE | FALSE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 248 | 42 |  | 663 | 0 | FALSE | FALSE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 30 | 0 |  | 168 | 0 | FALSE | TRUE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 62 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 62 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 113 | 0 |  | 451 | 0 | FALSE | TRUE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 269 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 191 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 177 | 419 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 479 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 94 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 92 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 120 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1595 | 1600 | -5 | 100 | -1050 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1370 | 1600 | -230 | 86 | -919 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1331 | 1600 | -269 | 83 | -891 | AC
BG_CO_00001 | N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [BG-MK] [OPP] TIE 400 kV CHERVENA MOGILA - STIP | XCM_ST11 VCMOGL11 1 | 1504 | 1890 | -386 | 80 | 1051 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1229 | 1587 | -358 | 77 | 811 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1176 | 1587 | -411 | 74 | 829 | AC
BG_MK_CO_00001 | N-1 TIE 400 kV CHERVENA MOGILA - STIP | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1370 | 1890 | -520 | 72 | 947 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1143 | 1587 | -444 | 72 | 796 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1141 | 1587 | -446 | 72 | 820 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1139 | 1587 | -448 | 72 | 794 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1129 | 1587 | -458 | 71 | 778 | AC

## 0930
Detailed results
Generated at: | 23/07/2026 23:35:14
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 1150
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2/[GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 527 | 379 |  | 902 | 0 | FALSE | FALSE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 246 | 421 |  | 421 | 0 | FALSE | FALSE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 232 | 0 |  | 663 | 0 | FALSE | TRUE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 53 | 0 |  | 168 | 0 | FALSE | TRUE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 108 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 108 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 265 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 197 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 193 | 419 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 304 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 88 | 0 |  | 314 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1595 | 1600 | -5 | 100 | -1047 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1415 | 1600 | -185 | 88 | -945 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1336 | 1600 | -264 | 83 | -893 | AC
BG_CO_00001 | N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [BG-MK] [OPP] TIE 400 kV CHERVENA MOGILA - STIP | XCM_ST11 VCMOGL11 1 | 1480 | 1890 | -410 | 78 | 1032 | AC
BG_MK_CO_00001 | N-1 TIE 400 kV CHERVENA MOGILA - STIP | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1415 | 1890 | -475 | 75 | 976 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1157 | 1587 | -430 | 73 | 801 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1149 | 1587 | -438 | 72 | 795 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1154 | 1600 | -446 | 72 | -778 | AC

## 1030
Detailed results
Generated at: | 23/07/2026 23:35:14
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2144
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1583 | 1587 | -4 | 100 | 1142 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1576 | 1587 | -11 | 99 | 1127 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1563 | 1600 | -37 | 98 | -1036 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1444 | 1587 | -143 | 91 | 1001 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1425 | 1600 | -175 | 89 | -955 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1408 | 1600 | -192 | 88 | -945 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1379 | 1587 | -208 | 87 | 995 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1368 | 1587 | -219 | 86 | 980 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1363 | 1587 | -224 | 86 | 940 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1343 | 1587 | -244 | 85 | 956 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1256 | 1587 | -331 | 79 | 871 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1258 | 1600 | -342 | 79 | -851 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1200 | 1600 | -400 | 75 | -811 | AC
BG_MK_CO_00001 | N-1 TIE 400 kV CHERVENA MOGILA - STIP | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1408 | 1890 | -482 | 75 | 975 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1147 | 1587 | -440 | 72 | 791 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1134 | 1587 | -453 | 71 | 817 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1132 | 1587 | -455 | 71 | 808 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1130 | 1587 | -457 | 71 | 815 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1135 | 1600 | -465 | 71 | -770 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1135 | 1600 | -465 | 71 | -770 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1133 | 1600 | -467 | 71 | -768 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1132 | 1600 | -468 | 71 | -767 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1119 | 1587 | -468 | 70 | 803 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1115 | 1587 | -472 | 70 | 800 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1113 | 1587 | -474 | 70 | 802 | AC

## 1130
Detailed results
Generated at: | 23/07/2026 23:35:14
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2545
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [OPP] OHL 400 kV Kardia - Vermio
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 223 | 7 |  | 902 | 0 | FALSE | FALSE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 110 | 385 |  | 421 | 0 | FALSE | FALSE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 193 | 291 |  | 663 | 0 | FALSE | FALSE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 85 | 0 |  | 168 | 0 | FALSE | TRUE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 172 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 172 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 253 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 112 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 0 | 419 |  | 419 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 275 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 40 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 8 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 10 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1581 | 1587 | -6 | 100 | 1135 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1480 | 1587 | -107 | 93 | 1048 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1469 | 1600 | -131 | 92 | -980 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1469 | 1600 | -131 | 92 | -983 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1414 | 1587 | -173 | 89 | 984 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1371 | 1600 | -229 | 86 | -923 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1353 | 1587 | -234 | 85 | 952 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1275 | 1587 | -312 | 80 | 919 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1252 | 1600 | -348 | 78 | -848 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1217 | 1587 | -370 | 77 | 810 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1209 | 1587 | -378 | 76 | 836 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1205 | 1600 | -395 | 75 | -816 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1166 | 1587 | -421 | 73 | 832 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1169 | 1600 | -431 | 73 | -805 | AC
BG_MK_CO_00001 | N-1 TIE 400 kV CHERVENA MOGILA - STIP | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1371 | 1890 | -519 | 73 | 951 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1153 | 1600 | -447 | 72 | -783 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1153 | 1600 | -447 | 72 | -783 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1132 | 1600 | -468 | 71 | -769 | AC

## 1230
Detailed results
Generated at: | 23/07/2026 23:35:14
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3344
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [OPP] OHL 400 kV Kardia - Vermio
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 223 | 3 |  | 902 | 0 | FALSE | FALSE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 110 | 0 |  | 421 | 0 | FALSE | TRUE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 192 | 69 |  | 663 | 0 | FALSE | FALSE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 93 | 168 |  | 168 | 0 | FALSE | FALSE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 187 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 187 | 231 |  | 340 | 0 | FALSE | FALSE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 255 | 525 |  | 838 | 0 | FALSE | FALSE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 111 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 0 | 419 |  | 419 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 40 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 8 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 10 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1582 | 1587 | -5 | 100 | 1124 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1509 | 1600 | -91 | 94 | -1009 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1509 | 1600 | -91 | 94 | -1011 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1496 | 1587 | -91 | 94 | 1021 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1485 | 1587 | -102 | 94 | -1047 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1457 | 1587 | -130 | 92 | 1044 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1371 | 1587 | -216 | 86 | 976 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1371 | 1587 | -216 | 86 | -946 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1370 | 1587 | -217 | 86 | -946 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1369 | 1587 | -218 | 86 | 948 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1359 | 1600 | -241 | 85 | -917 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1310 | 1587 | -277 | 83 | -921 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1314 | 1600 | -286 | 82 | -890 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1291 | 1587 | -296 | 81 | -911 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1291 | 1587 | -296 | 81 | 873 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1296 | 1600 | -304 | 81 | -914 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1272 | 1587 | -315 | 80 | -895 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1587 | -321 | 80 | -892 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1251 | 1587 | -336 | 79 | 873 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1249 | 1587 | -338 | 79 | 897 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1258 | 1600 | -342 | 79 | -853 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1258 | 1600 | -342 | 79 | -853 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1255 | 1600 | -345 | 78 | -851 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1244 | 1587 | -343 | 78 | 887 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1239 | 1587 | -348 | 78 | 850 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1587 | -354 | 78 | -871 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1242 | 1600 | -358 | 78 | -843 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1587 | -357 | 77 | -867 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1208 | 1587 | -379 | 76 | 862 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1587 | -397 | 75 | -840 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1194 | 1600 | -406 | 75 | -829 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1180 | 1587 | -408 | 74 | 841 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1167 | 1587 | -420 | 74 | 833 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1176 | 1600 | -424 | 74 | -800 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1587 | -425 | 73 | -821 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1160 | 1587 | -427 | 73 | 784 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1161 | 1600 | -439 | 73 | -790 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1155 | 1600 | -445 | 72 | -786 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1152 | 1600 | -448 | 72 | -784 | AC
BG_MK_CO_00001 | N-1 TIE 400 kV CHERVENA MOGILA - STIP | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1359 | 1890 | -531 | 72 | 945 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1148 | 1600 | -452 | 72 | -782 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1600 | -456 | 72 | -809 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1128 | 1587 | -459 | 71 | 809 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1127 | 1587 | -460 | 71 | 759 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1136 | 1600 | -464 | 71 | -787 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1120 | 1587 | -467 | 71 | 801 | AC

## 1330
Detailed results
Generated at: | 23/07/2026 23:35:14
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3532
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [OPP] OHL 400 kV Kardia - Vermio
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 211 | 0 |  | 902 | 0 | FALSE | TRUE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 104 | 33 |  | 421 | 0 | FALSE | FALSE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 182 | 164 |  | 663 | 0 | FALSE | FALSE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 90 | 0 |  | 168 | 0 | FALSE | TRUE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 182 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 182 | 206 |  | 340 | 0 | FALSE | FALSE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 202 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 106 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 0 | 419 |  | 419 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 492 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 38 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 7 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 10 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1582 | 1587 | -5 | 100 | -1110 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1569 | 1600 | -31 | 98 | -1044 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1568 | 1600 | -32 | 98 | -1040 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1556 | 1587 | -31 | 98 | 1085 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1553 | 1587 | -34 | 98 | 1101 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1476 | 1587 | -111 | 93 | 980 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1453 | 1587 | -134 | 92 | -993 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1453 | 1587 | -134 | 92 | -992 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1452 | 1587 | -135 | 91 | 1005 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1423 | 1587 | -164 | 90 | 964 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1423 | 1600 | -177 | 89 | -955 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1411 | 1587 | -176 | 89 | -989 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1401 | 1587 | -186 | 88 | -981 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1394 | 1600 | -206 | 87 | -976 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1379 | 1600 | -221 | 86 | -929 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1355 | 1587 | -232 | 85 | -948 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1348 | 1587 | -239 | 85 | -945 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1341 | 1587 | -246 | 85 | -942 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1334 | 1587 | -253 | 84 | 890 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1316 | 1587 | -271 | 83 | 939 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1327 | 1600 | -273 | 83 | -893 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1326 | 1600 | -274 | 83 | -892 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1313 | 1587 | -274 | 83 | -922 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1310 | 1587 | -277 | 83 | 923 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1317 | 1600 | -283 | 82 | -889 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1301 | 1600 | -299 | 81 | -878 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1289 | 1587 | -298 | 81 | -906 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1240 | 1587 | -347 | 78 | -872 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1246 | 1600 | -354 | 78 | -842 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1239 | 1600 | -361 | 77 | -856 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1226 | 1587 | -361 | 77 | 816 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1220 | 1587 | -367 | 77 | 868 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1600 | -374 | 77 | -863 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1212 | 1587 | -375 | 76 | 852 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1220 | 1600 | -380 | 76 | -826 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1204 | 1587 | -383 | 76 | 841 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1212 | 1600 | -388 | 76 | -821 | AC
BG_MK_CO_00001 | N-1 TIE 400 kV CHERVENA MOGILA - STIP | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1423 | 1890 | -467 | 75 | 986 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1205 | 1600 | -395 | 75 | -816 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1201 | 1600 | -399 | 75 | -814 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1197 | 1600 | -403 | 75 | -824 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1587 | -405 | 74 | -833 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1176 | 1587 | -411 | 74 | 840 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1587 | -412 | 74 | -828 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1587 | -412 | 74 | -827 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1168 | 1587 | -419 | 74 | 823 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1174 | 1600 | -426 | 73 | -797 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1587 | -424 | 73 | -821 | AC
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1169 | 1600 | -431 | 73 | -794 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1587 | -429 | 73 | -817 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1587 | -430 | 73 | -816 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1167 | 1600 | -433 | 73 | -790 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1163 | 1600 | -437 | 73 | -790 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1163 | 1600 | -437 | 73 | -786 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1587 | -435 | 73 | -813 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1161 | 1600 | -439 | 73 | -789 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1587 | -436 | 73 | -812 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1157 | 1600 | -443 | 72 | -786 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1157 | 1600 | -443 | 72 | -786 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1587 | -439 | 72 | -810 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1587 | -441 | 72 | -811 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1155 | 1600 | -445 | 72 | -785 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1587 | -442 | 72 | -808 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1154 | 1600 | -446 | 72 | -785 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1144 | 1587 | -443 | 72 | -782 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1587 | -443 | 72 | -808 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1142 | 1587 | -445 | 72 | -806 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1141 | 1587 | -446 | 72 | -805 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1141 | 1587 | -446 | 72 | -805 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1150 | 1600 | -450 | 72 | -782 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1149 | 1600 | -451 | 72 | -781 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1148 | 1600 | -452 | 72 | -781 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1139 | 1587 | -448 | 72 | -802 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1138 | 1587 | -448 | 72 | -803 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1138 | 1587 | -449 | 72 | -803 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1146 | 1600 | -454 | 72 | -780 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1136 | 1587 | -451 | 72 | -802 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1145 | 1600 | -455 | 72 | -778 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1587 | -452 | 72 | -802 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1587 | -452 | 72 | -804 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1135 | 1587 | -452 | 72 | -780 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1144 | 1600 | -456 | 72 | -777 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1133 | 1587 | -454 | 71 | 808 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1587 | -455 | 71 | -799 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1587 | -455 | 71 | -799 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1141 | 1600 | -459 | 71 | -776 | AC
Base case | Base case | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1141 | 1600 | -459 | 71 | -776 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1141 | 1600 | -459 | 71 | -776 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1141 | 1600 | -459 | 71 | -776 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1131 | 1587 | -456 | 71 | 745 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1140 | 1600 | -460 | 71 | -776 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1140 | 1600 | -460 | 71 | -775 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1139 | 1600 | -461 | 71 | -775 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1129 | 1587 | -458 | 71 | -797 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1124 | 1587 | -463 | 71 | 792 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1119 | 1587 | -468 | 71 | 798 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1124 | 1600 | -476 | 70 | -765 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1123 | 1600 | -477 | 70 | -776 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1112 | 1587 | -475 | 70 | -787 | AC

## 1430
Detailed results
Generated at: | 23/07/2026 23:35:14
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3528
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [OPP] OHL 400 kV Kardia - Vermio
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 219 | 0 |  | 902 | 0 | FALSE | TRUE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 108 | 109 |  | 421 | 0 | FALSE | FALSE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 157 | 127 |  | 663 | 0 | FALSE | FALSE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 92 | 0 |  | 168 | 0 | FALSE | TRUE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 185 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 185 | 161 |  | 340 | 0 | FALSE | FALSE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 188 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 109 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 9 | 419 |  | 419 | 0 | FALSE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 493 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 39 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 8 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 10 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1586 | 1587 | -1 | 100 | 1088 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1586 | 1587 | -1 | 100 | 1079 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1599 | 1600 | -1 | 100 | -1059 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1599 | 1600 | -1 | 100 | -1055 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1581 | 1587 | -6 | 100 | -1104 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1486 | 1587 | -101 | 94 | 1007 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1472 | 1600 | -128 | 92 | -984 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1456 | 1587 | -131 | 92 | 998 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1440 | 1587 | -147 | 91 | 965 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1435 | 1587 | -152 | 90 | -977 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1434 | 1587 | -153 | 90 | -976 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1417 | 1587 | -170 | 89 | -987 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1416 | 1587 | -171 | 89 | -987 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1418 | 1600 | -182 | 89 | -987 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1410 | 1600 | -190 | 88 | -946 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1368 | 1587 | -219 | 86 | -953 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1360 | 1587 | -227 | 86 | -949 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1355 | 1587 | -232 | 85 | 907 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1347 | 1587 | -240 | 85 | -942 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1356 | 1600 | -244 | 85 | -909 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1356 | 1600 | -244 | 85 | -909 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1344 | 1600 | -256 | 84 | -904 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1330 | 1587 | -257 | 84 | -930 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1325 | 1600 | -275 | 83 | -891 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1312 | 1587 | -275 | 83 | -920 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1308 | 1587 | -279 | 82 | 899 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1307 | 1587 | -280 | 82 | 905 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1272 | 1600 | -328 | 79 | -857 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1252 | 1587 | -335 | 79 | -876 | AC
BG_MK_CO_00001 | N-1 TIE 400 kV CHERVENA MOGILA - STIP | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1472 | 1890 | -418 | 78 | 1017 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1246 | 1600 | -354 | 78 | -841 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1243 | 1600 | -357 | 78 | -840 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1242 | 1600 | -358 | 78 | -858 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1600 | -365 | 77 | -866 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1233 | 1600 | -367 | 77 | -833 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1230 | 1600 | -370 | 77 | -830 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1212 | 1587 | -375 | 76 | 830 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1210 | 1587 | -377 | 76 | 836 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1205 | 1587 | -382 | 76 | 824 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1587 | -394 | 75 | -838 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1201 | 1600 | -399 | 75 | -814 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1587 | -399 | 75 | -833 | AC
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1197 | 1600 | -403 | 75 | -811 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1587 | -400 | 75 | -832 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1195 | 1600 | -405 | 75 | -805 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1195 | 1600 | -405 | 75 | -824 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1191 | 1600 | -409 | 74 | -807 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1191 | 1600 | -409 | 74 | -803 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1180 | 1587 | -407 | 74 | 816 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1189 | 1600 | -411 | 74 | -806 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1185 | 1600 | -415 | 74 | -804 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1185 | 1600 | -415 | 74 | -803 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1587 | -414 | 74 | -824 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1183 | 1600 | -417 | 74 | -802 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1181 | 1600 | -419 | 74 | -801 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1179 | 1600 | -421 | 74 | -800 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1169 | 1587 | -418 | 74 | 802 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1587 | -418 | 74 | -821 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1587 | -420 | 74 | -820 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1177 | 1600 | -423 | 74 | -798 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1166 | 1587 | -420 | 74 | 808 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1176 | 1600 | -424 | 74 | -798 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1174 | 1600 | -426 | 73 | -797 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1174 | 1600 | -426 | 73 | -796 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1172 | 1600 | -428 | 73 | -794 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1587 | -425 | 73 | -816 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1587 | -425 | 73 | -816 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1587 | -427 | 73 | -816 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1169 | 1600 | -431 | 73 | -793 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1169 | 1600 | -431 | 73 | -793 | AC
Base case | Base case | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1169 | 1600 | -431 | 73 | -793 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1169 | 1600 | -431 | 73 | -793 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1168 | 1600 | -432 | 73 | -793 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1168 | 1600 | -432 | 73 | -793 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1587 | -429 | 73 | -813 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1167 | 1600 | -433 | 73 | -792 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1156 | 1587 | -431 | 73 | -812 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1154 | 1587 | -433 | 73 | -812 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1154 | 1587 | -433 | 73 | -811 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1587 | -435 | 73 | -809 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1587 | -435 | 73 | -809 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1587 | -436 | 73 | -809 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1587 | -438 | 72 | -808 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1587 | -438 | 72 | -806 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1587 | -438 | 72 | -809 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1587 | -439 | 72 | -807 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1587 | -439 | 72 | -807 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1587 | -441 | 72 | -806 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1156 | 1600 | -444 | 72 | -783 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1155 | 1600 | -445 | 72 | -784 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1587 | -444 | 72 | -803 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1587 | -447 | 72 | -801 | AC
BG_GR_CO_00002 | N-1 TIE 400 kV MARITSA IZTOK-NEA SANTA CK. 1 | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1344 | 1890 | -546 | 71 | 931 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1128 | 1587 | -459 | 71 | 772 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1127 | 1587 | -460 | 71 | -768 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1125 | 1587 | -462 | 71 | -792 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1125 | 1587 | -462 | 71 | 777 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1116 | 1587 | -471 | 70 | -784 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1123 | 1600 | -477 | 70 | -760 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1123 | 1600 | -477 | 70 | -777 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1112 | 1587 | -475 | 70 | 764 | AC

## 1530
Detailed results
Generated at: | 23/07/2026 23:35:14
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3510
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [OPP] OHL 400 kV Kardia - Vermio
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 223 | 0 |  | 902 | 0 | FALSE | TRUE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 109 | 394 |  | 421 | 0 | FALSE | FALSE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 32 | 129 |  | 663 | 0 | FALSE | FALSE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 87 | 0 |  | 168 | 0 | FALSE | TRUE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 176 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 176 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 191 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 111 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 114 | 419 |  | 419 | 0 | FALSE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 335 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 40 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 8 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 10 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1584 | 1587 | -3 | 100 | 1102 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1565 | 1587 | -22 | 99 | 1106 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1554 | 1587 | -33 | 98 | -1091 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1562 | 1600 | -38 | 98 | -1042 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1562 | 1600 | -38 | 98 | -1038 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1530 | 1587 | -57 | 96 | 1018 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1482 | 1587 | -105 | 93 | 1024 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1475 | 1587 | -112 | 93 | 1009 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1454 | 1587 | -133 | 92 | -1018 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1454 | 1600 | -146 | 91 | -1016 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1447 | 1600 | -153 | 90 | -972 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1420 | 1587 | -167 | 89 | -994 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1401 | 1587 | -186 | 88 | 947 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1395 | 1600 | -205 | 87 | -940 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1382 | 1587 | -205 | 87 | -970 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1378 | 1587 | -209 | 87 | -945 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1378 | 1587 | -209 | 87 | -944 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1367 | 1587 | -220 | 86 | -957 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1364 | 1587 | -223 | 86 | -959 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1360 | 1587 | -227 | 86 | -954 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1334 | 1587 | -253 | 84 | -937 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1336 | 1600 | -264 | 83 | -900 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1335 | 1600 | -265 | 83 | -900 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1317 | 1600 | -283 | 82 | -890 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1290 | 1600 | -310 | 81 | -873 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1260 | 1587 | -327 | 79 | -886 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1261 | 1600 | -339 | 79 | -853 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1241 | 1600 | -359 | 78 | -874 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1234 | 1600 | -366 | 77 | -837 | AC
BG_MK_CO_00001 | N-1 TIE 400 kV CHERVENA MOGILA - STIP | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1447 | 1890 | -443 | 77 | 1004 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1587 | -376 | 76 | -854 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1218 | 1600 | -382 | 76 | -827 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1205 | 1587 | -382 | 76 | 848 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1211 | 1600 | -389 | 76 | -822 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1207 | 1600 | -393 | 75 | -836 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1196 | 1587 | -391 | 75 | 853 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1205 | 1600 | -395 | 75 | -817 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1587 | -393 | 75 | -842 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -840 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1587 | -406 | 74 | -834 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1175 | 1587 | -412 | 74 | 825 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1587 | -413 | 74 | -829 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1587 | -418 | 74 | -825 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1587 | -418 | 74 | -825 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1587 | -418 | 74 | -825 | AC
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1177 | 1600 | -423 | 74 | -801 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1587 | -420 | 74 | -824 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1177 | 1600 | -423 | 74 | -801 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1167 | 1587 | -420 | 74 | 830 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1587 | -420 | 74 | -823 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1587 | -423 | 73 | -822 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1587 | -424 | 73 | -821 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1587 | -426 | 73 | -820 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1170 | 1600 | -430 | 73 | -794 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1587 | -427 | 73 | -819 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1587 | -427 | 73 | -819 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1168 | 1600 | -432 | 73 | -795 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1167 | 1600 | -433 | 73 | -791 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1167 | 1600 | -433 | 73 | -794 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1167 | 1600 | -433 | 73 | -794 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1587 | -430 | 73 | -817 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1587 | -430 | 73 | -817 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1163 | 1600 | -437 | 73 | -803 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1163 | 1600 | -437 | 73 | -792 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1153 | 1587 | -434 | 73 | 763 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1587 | -434 | 73 | -814 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1162 | 1600 | -438 | 73 | -791 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1161 | 1600 | -439 | 73 | -790 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1161 | 1600 | -439 | 73 | -790 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1587 | -436 | 73 | -811 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1587 | -436 | 73 | -814 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1587 | -437 | 72 | -812 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1159 | 1600 | -441 | 72 | -789 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1587 | -439 | 72 | -811 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1157 | 1600 | -443 | 72 | -788 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1155 | 1600 | -445 | 72 | -787 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1154 | 1600 | -446 | 72 | -787 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1152 | 1600 | -448 | 72 | -785 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1150 | 1600 | -450 | 72 | -783 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1150 | 1600 | -450 | 72 | -782 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1147 | 1600 | -453 | 72 | -782 | AC
Base case | Base case | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1147 | 1600 | -453 | 72 | -781 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1147 | 1600 | -453 | 72 | -781 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1146 | 1600 | -454 | 72 | -781 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1146 | 1600 | -454 | 72 | -781 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1130 | 1587 | -457 | 71 | 795 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1136 | 1600 | -464 | 71 | -773 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1135 | 1600 | -465 | 71 | -774 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1125 | 1587 | -462 | 71 | 740 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1124 | 1587 | -463 | 71 | 800 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1587 | -464 | 71 | -795 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1115 | 1587 | -472 | 70 | -790 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1111 | 1587 | -476 | 70 | -787 | AC

## 1630
Detailed results
Generated at: | 23/07/2026 23:35:15
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3434
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [OPP] OHL 400 kV Kardia - Vermio
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 234 | 0 |  | 902 | 0 | FALSE | TRUE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 115 | 421 |  | 421 | 0 | FALSE | FALSE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 80 | 0 |  | 168 | 0 | FALSE | TRUE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 161 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 161 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 202 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 117 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 156 | 419 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 49 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 89 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 29 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 38 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1595 | 1600 | -5 | 100 | -1062 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1594 | 1600 | -6 | 100 | -1058 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1550 | 1587 | -37 | 98 | 1041 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1498 | 1587 | -89 | 94 | 1040 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1448 | 1600 | -152 | 90 | -972 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1415 | 1587 | -172 | 89 | 995 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1411 | 1587 | -176 | 89 | 970 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1397 | 1587 | -190 | 88 | -981 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1386 | 1587 | -201 | 87 | 945 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1379 | 1587 | -208 | 87 | 932 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1356 | 1600 | -244 | 85 | -949 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1343 | 1600 | -257 | 84 | -926 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1341 | 1600 | -259 | 84 | -906 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1320 | 1587 | -267 | 83 | -925 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1316 | 1587 | -271 | 83 | -924 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1304 | 1587 | -283 | 82 | -913 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1297 | 1587 | -290 | 82 | -910 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1289 | 1587 | -298 | 81 | -906 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1290 | 1600 | -310 | 81 | -871 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1289 | 1600 | -311 | 81 | -871 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1279 | 1600 | -321 | 80 | -866 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1587 | -333 | 79 | -881 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1236 | 1587 | -351 | 78 | -868 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1236 | 1600 | -364 | 77 | -838 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1231 | 1600 | -369 | 77 | -841 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1227 | 1600 | -373 | 77 | -833 | AC
BG_MK_CO_00001 | N-1 TIE 400 kV CHERVENA MOGILA - STIP | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1448 | 1890 | -442 | 77 | 1004 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1214 | 1600 | -386 | 76 | -823 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1204 | 1587 | -383 | 76 | -828 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1203 | 1587 | -384 | 76 | -828 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1190 | 1600 | -410 | 74 | -809 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1187 | 1600 | -413 | 74 | -806 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1174 | 1587 | -413 | 74 | 800 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1180 | 1600 | -420 | 74 | -802 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1587 | -421 | 74 | -821 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1151 | 1587 | -436 | 73 | 803 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | -806 | AC
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1143 | 1600 | -457 | 71 | -779 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1136 | 1600 | -464 | 71 | -771 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1136 | 1600 | -464 | 71 | -772 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1136 | 1600 | -464 | 71 | -773 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1134 | 1600 | -466 | 71 | -773 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1133 | 1600 | -467 | 71 | -772 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1131 | 1600 | -469 | 71 | -771 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1587 | -466 | 71 | -789 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1130 | 1600 | -470 | 71 | -770 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1126 | 1600 | -474 | 70 | -767 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1124 | 1600 | -476 | 70 | -767 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1124 | 1600 | -476 | 70 | -766 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1122 | 1600 | -478 | 70 | -765 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1120 | 1600 | -480 | 70 | -763 | AC

## 1730
Detailed results
Generated at: | 23/07/2026 23:35:15
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3627
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [OPP] OHL 400 kV Kardia - Vermio
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 529 | 1 |  | 902 | 0 | FALSE | FALSE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 132 | 253 |  | 421 | 0 | FALSE | FALSE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 61 | 168 |  | 168 | 0 | FALSE | FALSE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 123 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 123 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 66 | 0 |  | 451 | 0 | FALSE | TRUE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 256 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 205 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 185 | 362 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 536 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 133 | 0 |  | 314 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1582 | 1587 | -5 | 100 | 1092 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1594 | 1600 | -6 | 100 | -1060 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1594 | 1600 | -6 | 100 | -1056 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1502 | 1587 | -85 | 95 | 1032 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1466 | 1587 | -121 | 92 | -1026 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1456 | 1587 | -131 | 92 | 988 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1441 | 1600 | -159 | 90 | -989 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1404 | 1587 | -183 | 88 | 947 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1393 | 1587 | -194 | 88 | -973 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1385 | 1600 | -215 | 87 | -964 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1381 | 1600 | -219 | 86 | -929 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1378 | 1600 | -222 | 86 | -944 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1364 | 1587 | -223 | 86 | -951 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1356 | 1587 | -231 | 85 | -948 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1354 | 1587 | -233 | 85 | -945 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1322 | 1587 | -265 | 83 | -924 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1313 | 1587 | -274 | 83 | 884 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1310 | 1587 | -277 | 83 | -918 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1303 | 1587 | -284 | 82 | 871 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1283 | 1587 | -304 | 81 | -877 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1282 | 1587 | -305 | 81 | -876 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1291 | 1600 | -309 | 81 | -874 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1280 | 1587 | -307 | 81 | 892 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1271 | 1587 | -316 | 80 | -890 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1258 | 1600 | -342 | 79 | -850 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1258 | 1600 | -342 | 79 | -850 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1239 | 1600 | -361 | 77 | -840 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1202 | 1587 | -385 | 76 | 833 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1201 | 1587 | -386 | 76 | 836 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1210 | 1600 | -390 | 76 | -821 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1208 | 1600 | -392 | 76 | -820 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1190 | 1600 | -410 | 74 | -807 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | -831 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1587 | -416 | 74 | -822 | AC
BG_MK_CO_00001 | N-1 TIE 400 kV CHERVENA MOGILA - STIP | [BG-GR] [OPP] TIE 400 kV BLAGOEVGRAD - LAGADAS | XBG_LA11 VBLAGO11 1 | 1381 | 1890 | -509 | 73 | 958 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1156 | 1587 | -431 | 73 | 806 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1155 | 1587 | -432 | 73 | 790 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1163 | 1600 | -437 | 73 | -790 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1587 | -436 | 73 | -809 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1587 | -438 | 72 | -806 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1154 | 1600 | -446 | 72 | -784 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1124 | 1587 | -463 | 71 | 778 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1119 | 1587 | -468 | 71 | -786 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1116 | 1587 | -471 | 70 | -785 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1113 | 1587 | -474 | 70 | -783 | AC

## 1830
Detailed results
Generated at: | 23/07/2026 23:35:15
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3433
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2/[GR-GR] [OPP] OHL 400 kV Kardia - Vermio
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 531 | 0 |  | 902 | 0 | FALSE | TRUE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 133 | 0 |  | 421 | 0 | FALSE | TRUE
GR_RA_00008 | GR | GPTOLE11_generator | 0 | 663 |  |  | 0 | 42 |  | 663 | 0 | TRUE | FALSE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 38 | 168 |  | 168 | 0 | FALSE | FALSE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 76 | 157 |  | 340 | 0 | FALSE | FALSE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 76 | 340 |  | 340 | 0 | FALSE | FALSE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 247 | 0 |  | 451 | 0 | FALSE | TRUE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 270 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 190 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 166 | 155 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 536 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 166 | 0 |  | 314 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1582 | 1587 | -5 | 100 | 1127 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1478 | 1587 | -109 | 93 | 1048 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1478 | 1587 | -109 | 93 | 1049 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1433 | 1587 | -154 | 90 | -1011 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1382 | 1587 | -205 | 87 | 985 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1392 | 1600 | -208 | 87 | -941 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1390 | 1600 | -210 | 87 | -938 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1366 | 1587 | -221 | 86 | 946 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1316 | 1587 | -271 | 83 | -910 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1315 | 1587 | -272 | 83 | -911 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1315 | 1587 | -272 | 83 | 927 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1300 | 1600 | -300 | 81 | -898 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1281 | 1587 | -306 | 81 | 907 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1280 | 1587 | -307 | 81 | -902 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1280 | 1587 | -307 | 81 | 913 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1276 | 1587 | -311 | 80 | 907 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1269 | 1587 | -318 | 80 | -893 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1265 | 1587 | -322 | 80 | -890 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1263 | 1587 | -324 | 80 | -889 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1262 | 1587 | -325 | 80 | 875 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1256 | 1587 | -331 | 79 | 896 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1265 | 1600 | -335 | 79 | -892 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1242 | 1587 | -345 | 78 | -876 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1251 | 1600 | -349 | 78 | -850 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1193 | 1587 | -394 | 75 | 852 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1587 | -403 | 75 | -835 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1180 | 1587 | -407 | 74 | 836 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1174 | 1587 | -413 | 74 | 835 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1156 | 1587 | -431 | 73 | 820 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1165 | 1600 | -435 | 73 | -796 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1154 | 1587 | -433 | 73 | 824 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1150 | 1587 | -437 | 72 | 818 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1587 | -441 | 72 | -810 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1139 | 1600 | -461 | 71 | -778 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1139 | 1600 | -461 | 71 | -778 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1122 | 1587 | -465 | 71 | 801 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1131 | 1600 | -469 | 71 | -772 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1121 | 1587 | -466 | 71 | 800 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1120 | 1587 | -467 | 71 | 800 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1120 | 1587 | -467 | 71 | 799 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1117 | 1587 | -470 | 70 | 798 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1117 | 1587 | -470 | 70 | 797 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1117 | 1587 | -470 | 70 | 798 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1116 | 1587 | -471 | 70 | 797 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1116 | 1587 | -471 | 70 | 797 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1116 | 1587 | -471 | 70 | 797 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1116 | 1587 | -471 | 70 | 797 | AC
Base case | Base case | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1116 | 1587 | -471 | 70 | 797 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1116 | 1587 | -471 | 70 | 784 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1116 | 1587 | -471 | 70 | 797 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1116 | 1587 | -471 | 70 | 797 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1116 | 1587 | -471 | 70 | 796 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1116 | 1587 | -471 | 70 | 797 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1116 | 1587 | -472 | 70 | 797 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1115 | 1587 | -472 | 70 | 797 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1115 | 1587 | -472 | 70 | 795 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1115 | 1587 | -472 | 70 | 796 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1115 | 1587 | -472 | 70 | 796 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1115 | 1587 | -472 | 70 | 796 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1113 | 1587 | -474 | 70 | 795 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1113 | 1587 | -474 | 70 | 795 | AC

## 1930
Detailed results
Generated at: | 23/07/2026 23:35:15
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3111
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2/[GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 487 | 432 |  | 902 | 0 | FALSE | FALSE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 122 | 0 |  | 421 | 0 | FALSE | TRUE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 13 | 0 |  | 168 | 0 | FALSE | TRUE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 27 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 27 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 239 | 0 |  | 451 | 0 | FALSE | TRUE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 227 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 175 | 450 |  | 450 | 0 | FALSE | FALSE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 152 | 0 |  | 419 | 0 | FALSE | TRUE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 451 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 176 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 79 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 103 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1596 | 1600 | -4 | 100 | -1055 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1400 | 1600 | -200 | 87 | -938 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1353 | 1587 | -234 | 85 | -947 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1338 | 1587 | -249 | 84 | 933 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1324 | 1587 | -263 | 83 | 922 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1324 | 1587 | -263 | 83 | 913 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1322 | 1587 | -265 | 83 | -931 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1297 | 1587 | -290 | 82 | 895 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1294 | 1600 | -306 | 81 | -887 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1271 | 1600 | -329 | 79 | -894 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1254 | 1600 | -346 | 78 | -844 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1241 | 1587 | -346 | 78 | -874 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1587 | -348 | 78 | -873 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1587 | -352 | 78 | -869 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1227 | 1587 | -360 | 77 | 856 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1214 | 1587 | -373 | 77 | 848 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1212 | 1600 | -388 | 76 | -819 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1194 | 1600 | -406 | 75 | -809 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1172 | 1600 | -428 | 73 | -793 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1167 | 1600 | -433 | 73 | -791 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1166 | 1600 | -434 | 73 | -790 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1154 | 1587 | -433 | 73 | -814 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1142 | 1587 | -445 | 72 | -806 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1135 | 1587 | -452 | 72 | -787 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1135 | 1587 | -452 | 71 | -788 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1134 | 1587 | -453 | 71 | 791 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1587 | -454 | 71 | -800 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1134 | 1600 | -466 | 71 | -768 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1120 | 1587 | -467 | 71 | 770 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1119 | 1587 | -468 | 70 | 780 | AC

## 2030
Detailed results
Generated at: | 23/07/2026 23:35:15
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | North-Greece Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3425
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2/[GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
GR_RA_00003 | GR | GKO_PW11_generator | 0 | 902 |  |  | 417 | 107 |  | 902 | 0 | FALSE | FALSE
GR_RA_00004 | GR | GENTHE13_generator | 0 | 421 |  |  | 104 | 0 |  | 421 | 0 | FALSE | TRUE
GR_RA_00009 | GR | GK_VER13_generator | 0 | 168 |  |  | 1 | 0 |  | 168 | 0 | FALSE | TRUE
GR_RA_00011 | GR | GAMIDE17_generator | 0 | 340 |  |  | 2 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00012 | GR | GAMIDE18_generator | 0 | 340 |  |  | 2 | 0 |  | 340 | 0 | FALSE | TRUE
GR_RA_00013 | GR | GAGNIK11_generator | 0 | 451 |  |  | 183 | 0 |  | 451 | 0 | FALSE | TRUE
GR_RA_00014 | GR | GAGN2_11_generator | 0 | 838 |  |  | 182 | 0 |  | 838 | 0 | FALSE | TRUE
GR_RA_00015 | GR | G2IRON11_generator | 0 | 450 |  |  | 91 | 0 |  | 450 | 0 | FALSE | TRUE
GR_RA_00016 | GR | GKALIV11_generator | 0 | 419 |  |  | 121 | 234 |  | 419 | 0 | FALSE | FALSE
GR_RA_00017 | GR | GKLAVR11_generator | 0 | 494 |  |  | 0 | 494 |  | 494 | 0 | TRUE | FALSE
GR_RA_00018 | GR | GKLAVR12_generator | 0 | 536 |  |  | 0 | 536 |  | 536 | 0 | TRUE | FALSE
GR_RA_00019 | GR | G5MEGA14_generator | 0 | 314 |  |  | 152 | 0 |  | 314 | 0 | FALSE | TRUE
GR_RA_00020 | GR | GKREMA31_generator | 0 | 190 |  |  | 49 | 0 |  | 190 | 0 | FALSE | TRUE
GR_RA_00021 | GR | GKREMA32_generator | 0 | 247 |  |  | 64 | 0 |  | 247 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1597 | 1600 | -3 | 100 | -1057 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1551 | 1600 | -49 | 97 | -1032 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1511 | 1600 | -89 | 94 | -1040 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1415 | 1600 | -185 | 88 | -974 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1403 | 1587 | -184 | 88 | -987 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1372 | 1587 | -215 | 86 | -960 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1343 | 1587 | -244 | 85 | 935 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1342 | 1587 | -245 | 85 | 926 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1337 | 1587 | -250 | 84 | -938 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1327 | 1587 | -260 | 84 | 923 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1328 | 1600 | -272 | 83 | -933 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1312 | 1587 | -275 | 83 | -922 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1306 | 1587 | -281 | 82 | 901 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1292 | 1587 | -295 | 81 | -910 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1289 | 1600 | -311 | 81 | -869 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1270 | 1600 | -330 | 79 | -859 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1248 | 1600 | -352 | 78 | -842 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1236 | 1587 | -351 | 78 | 862 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1244 | 1600 | -356 | 78 | -841 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1243 | 1600 | -357 | 78 | -840 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1220 | 1587 | -367 | 77 | 852 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1587 | -369 | 77 | -858 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1225 | 1600 | -375 | 77 | -828 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1214 | 1587 | -373 | 76 | -840 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1587 | -374 | 76 | -856 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1213 | 1587 | -374 | 76 | -841 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1587 | -384 | 76 | -849 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1194 | 1600 | -406 | 75 | -809 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1188 | 1600 | -412 | 74 | -804 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1157 | 1600 | -443 | 72 | -797 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1156 | 1600 | -444 | 72 | -816 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1137 | 1587 | -450 | 72 | -803 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1145 | 1600 | -455 | 72 | -776 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1133 | 1600 | -467 | 71 | -768 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1587 | -464 | 71 | -792 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1128 | 1600 | -472 | 71 | -765 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1118 | 1587 | -469 | 70 | 779 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1116 | 1587 | -471 | 70 | 768 | AC

## 2130
Detailed results
Generated at: | 23/07/2026 23:35:15
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3254.56
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2/[GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1584 | 1600 | -16 | 99 | -1042 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1468 | 1587 | -119 | 92 | 1009 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1461 | 1587 | -126 | 92 | 1003 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1459 | 1587 | -128 | 92 | 999 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1446 | 1587 | -141 | 91 | -999 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1435 | 1587 | -152 | 90 | 979 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1421 | 1600 | -179 | 89 | -952 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1405 | 1587 | -182 | 89 | -985 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1394 | 1600 | -206 | 87 | -969 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1364 | 1587 | -223 | 86 | 939 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1352 | 1587 | -235 | 85 | -946 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1351 | 1587 | -236 | 85 | 930 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1348 | 1600 | -252 | 84 | -927 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1330 | 1587 | -257 | 84 | -929 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1322 | 1587 | -265 | 83 | -926 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1297 | 1600 | -303 | 81 | -882 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1247 | 1587 | -340 | 79 | -875 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1587 | -353 | 78 | -867 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1587 | -354 | 78 | -865 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1211 | 1600 | -389 | 76 | -821 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1184 | 1587 | -403 | 75 | 821 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1183 | 1587 | -404 | 75 | -817 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1182 | 1587 | -405 | 74 | -816 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1189 | 1600 | -411 | 74 | -809 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1175 | 1587 | -412 | 74 | 812 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1172 | 1587 | -415 | 74 | 809 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1180 | 1600 | -420 | 74 | -800 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1180 | 1600 | -420 | 74 | -800 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1178 | 1600 | -422 | 74 | -799 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1587 | -423 | 73 | -813 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1600 | -429 | 73 | -824 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1587 | -429 | 73 | -815 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1151 | 1587 | -436 | 72 | 792 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1587 | -447 | 72 | -804 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1134 | 1587 | -453 | 71 | -800 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1131 | 1587 | -456 | 71 | -796 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1138 | 1600 | -462 | 71 | -773 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1127 | 1587 | -460 | 71 | -794 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1115 | 1587 | -472 | 70 | -784 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1112 | 1587 | -475 | 70 | -783 | AC

## 2230
Detailed results
Generated at: | 23/07/2026 23:35:15
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3426.71
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2/[GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1584 | 1600 | -16 | 99 | -1037 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1525 | 1587 | -62 | 96 | 1048 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1522 | 1587 | -65 | 96 | 1044 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1520 | 1587 | -67 | 96 | 1040 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1497 | 1587 | -90 | 94 | 1022 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1489 | 1600 | -111 | 93 | -988 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1463 | 1587 | -124 | 92 | -1010 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1460 | 1600 | -140 | 91 | -997 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1447 | 1587 | -140 | 91 | -1014 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1437 | 1600 | -163 | 90 | -998 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1420 | 1587 | -167 | 89 | 979 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1409 | 1587 | -178 | 89 | 971 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1403 | 1600 | -197 | 88 | -947 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1391 | 1587 | -196 | 88 | -974 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1385 | 1587 | -202 | 87 | -966 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1353 | 1587 | -234 | 85 | -948 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1299 | 1587 | -288 | 82 | -910 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1279 | 1587 | -308 | 81 | -897 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1265 | 1587 | -322 | 80 | -889 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1226 | 1587 | -361 | 77 | -846 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1226 | 1587 | -361 | 77 | -846 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1235 | 1600 | -365 | 77 | -831 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1217 | 1587 | -370 | 77 | 844 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1225 | 1600 | -375 | 77 | -827 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1212 | 1587 | -375 | 76 | 839 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1210 | 1587 | -377 | 76 | 836 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1209 | 1600 | -391 | 76 | -814 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1208 | 1600 | -392 | 76 | -814 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | -848 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -832 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -838 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1189 | 1587 | -398 | 75 | 820 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1192 | 1600 | -408 | 75 | -803 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1174 | 1600 | -426 | 73 | -792 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1587 | -424 | 73 | -820 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1587 | -432 | 73 | -814 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1587 | -436 | 73 | -813 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1587 | -442 | 72 | -808 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1587 | -444 | 72 | -803 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1139 | 1587 | -448 | 72 | -802 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1145 | 1600 | -455 | 72 | -774 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1145 | 1600 | -455 | 72 | -773 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1587 | -452 | 72 | -801 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1587 | -461 | 71 | -794 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1125 | 1587 | -462 | 71 | -793 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1124 | 1587 | -463 | 71 | -793 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1587 | -465 | 71 | -791 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1587 | -465 | 71 | -789 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1587 | -466 | 71 | -791 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1587 | -466 | 71 | -791 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1120 | 1587 | -467 | 71 | -790 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1118 | 1587 | -469 | 70 | -790 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1118 | 1587 | -469 | 70 | -789 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1122 | 1600 | -478 | 70 | -759 | AC

## 2330
Detailed results
Generated at: | 23/07/2026 23:35:15
Business day: | 2026-07-25
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | North-Greece Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3500.12
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [DIR] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1585 | 1587 | -2 | 100 | -1111 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1514 | 1600 | -86 | 95 | -1055 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1495 | 1587 | -92 | 94 | -1037 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1484 | 1587 | -103 | 93 | 1024 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1483 | 1587 | -104 | 93 | 1023 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1481 | 1587 | -106 | 93 | 1019 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1460 | 1587 | -127 | 92 | 1002 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1459 | 1587 | -128 | 92 | -1021 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1457 | 1587 | -130 | 92 | -1018 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1452 | 1587 | -135 | 91 | -1017 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1435 | 1587 | -152 | 90 | -1006 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1420 | 1587 | -167 | 89 | -995 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1406 | 1600 | -194 | 88 | -936 | AC
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1372 | 1587 | -215 | 86 | 950 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-GR] [DIR] OHL 400 kV Thessaloniki - Agios Dimitrios | GTHESS13 GAGDIM13 1 | 1363 | 1587 | -224 | 86 | 944 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1373 | 1600 | -227 | 86 | -921 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1359 | 1587 | -228 | 86 | -956 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1359 | 1587 | -228 | 86 | -937 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1358 | 1587 | -229 | 86 | -936 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1310 | 1600 | -290 | 82 | -877 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1300 | 1600 | -300 | 81 | -889 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1286 | 1587 | -301 | 81 | -905 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1289 | 1600 | -311 | 81 | -907 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1273 | 1587 | -314 | 80 | -893 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1587 | -325 | 80 | -890 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1587 | -341 | 78 | -879 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1236 | 1587 | -351 | 78 | -874 | AC
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1587 | -353 | 78 | -869 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1587 | -357 | 77 | -869 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1587 | -358 | 77 | -867 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1587 | -359 | 77 | -869 | AC
Base case | Base case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1587 | -368 | 77 | -861 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1587 | -368 | 77 | -861 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1587 | -368 | 77 | -861 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1587 | -370 | 77 | -859 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1587 | -370 | 77 | -859 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1587 | -371 | 77 | -858 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -855 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -858 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1587 | -372 | 77 | -858 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1587 | -373 | 76 | -857 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1587 | -373 | 76 | -857 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1587 | -376 | 76 | -856 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1587 | -379 | 76 | -853 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1587 | -380 | 76 | -853 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1587 | -382 | 76 | -851 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1587 | -387 | 76 | -847 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1587 | -395 | 75 | -842 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1587 | -410 | 74 | -833 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Amydeo - Ptolemaida | GKPTOL12 GAMIDE14 1 | 1163 | 1587 | -424 | 73 | 810 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1587 | -426 | 73 | -819 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Amydeo - Vermio | GAMIDE16 GK_VER11 1 | 1159 | 1587 | -428 | 73 | 806 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [OPP] OHL 400 kV Kardia - Vermio | GKARDI11 GK_VER12 1 | 1157 | 1587 | -430 | 73 | 804 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1152 | 1600 | -448 | 72 | -782 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1152 | 1600 | -448 | 72 | -781 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-GR] [DIR] OHL 400 kV Kardia - Ptolemaida | GKPTOL13 GKARDI13 1 | 1139 | 1587 | -448 | 72 | 790 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1587 | -452 | 72 | -798 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1127 | 1587 | -460 | 71 | -799 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1134 | 1600 | -466 | 71 | -772 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11 GLAGAD11 1 | 1121 | 1600 | -479 | 70 | -761 | AC