## SRO borders-exports
SUBMISSION DATE: | 26.07.2026
BUSINESS DATE: | 27.07.2026
1st ID CC Results
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC RO-BG
00:00 | 01:00 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3652 | 3452 | 2416
01:00 | 02:00 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 97 | 3826 | 3626 | 2538
02:00 | 03:00 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 95 | 3827 | 3627 | 2539
03:00 | 04:00 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 98 | 3845 | 3645 | 2551
04:00 | 05:00 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 97 | 3837 | 3637 | 2546
05:00 | 06:00 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 94 | 3803 | 3603 | 2522
06:00 | 07:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 2789 | 2589 | 1812
07:00 | 08:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 99 | 1346 | 1146 | 802
08:00 | 09:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 99 | 708 | 508 | 355
09:00 | 10:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 99 | 864 | 664 | 464
10:00 | 11:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 1505 | 1305 | 913
11:00 | 12:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 1928 | 1728 | 1209
12:00 | 13:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 2415 | 2215 | 1550
13:00 | 14:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 2903 | 2703 | 1892
14:00 | 15:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3031 | 2831 | 1981
15:00 | 16:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 99 | 2574 | 2374 | 1661
16:00 | 17:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 99 | 2001 | 1801 | 1260
17:00 | 18:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3444 | 3244 | 2270
18:00 | 19:00 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 2973 | 2773 | 1940
19:00 | 20:00 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 1756 | 1556 | 1088
20:00 | 21:00 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 1642 | 1442 | 1009
21:00 | 22:00 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 1452 | 1252 | 876
22:00 | 23:00 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 1771 | 1571 | 1099
23:00 | 00:00 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3041 | 2841 | 1989

## SRO borders-imports
SUBMISSION DATE: | 26.07.2026
BUSINESS DATE: | 27.07.2026
1st ID CC Results
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC BG-RO
00:00 | 01:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 99 | 3121 | 2921 | 2045
01:00 | 02:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3412 | 3212 | 2248
02:00 | 03:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3475 | 3275 | 2292
03:00 | 04:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3407 | 3207 | 2245
04:00 | 05:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3409 | 3209 | 2246
05:00 | 06:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3383 | 3183 | 2227
06:00 | 07:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 3321 | 3121 | 2184
07:00 | 08:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 3288 | 3088 | 2161
08:00 | 09:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 2344 | 2144 | 1500
09:00 | 10:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 2229 | 2029 | 1420
10:00 | 11:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 2692 | 2492 | 1744
11:00 | 12:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 2952 | 2752 | 1926
12:00 | 13:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3229 | 3029 | 2120
13:00 | 14:00 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3366 | 3166 | 2215
14:00 | 15:00 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3292 | 3092 | 2164
15:00 | 16:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3397 | 3197 | 2237
16:00 | 17:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3151 | 2951 | 2065
17:00 | 18:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3367 | 3167 | 2216
18:00 | 19:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3317 | 3117 | 2181
19:00 | 20:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 2748 | 2548 | 1783
20:00 | 21:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 2752 | 2552 | 1786
21:00 | 22:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 2637 | 2437 | 1705
22:00 | 23:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 2737 | 2537 | 1775
23:00 | 00:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 3290 | 3090 | 2162

## SRO borders-exports RAs
SUBMISSION DATE: | 26.07.2026
BUSINESS DATE: | 27.07.2026
1st ID CC Remedial Actions
Name of the RA | RA ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00008 | topological | helpful | notApplied | notApplied | notApplied | notApplied | notApplied | helpful | notApplied | notApplied | notApplied | notApplied | helpful | helpful | helpful | notApplied | helpful | helpful | helpful | helpful | notApplied | notApplied | notApplied | notApplied | helpful
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00009 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | notApplied | notApplied | notApplied | notApplied | notApplied | helpful | helpful | helpful | helpful | notApplied | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00017 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV TINTARENI-KOZLODUI 1 | BG_RA_00001 | topological |  | helpful | helpful | helpful | helpful | helpful | [8 empty] | helpful
PRA 400 kV TINTARENI-KOZLODUI 2 | BG_RA_00002 | topological |  | notApplied | notApplied | notApplied | notApplied | notApplied

## SRO borders-imports RAs
SUBMISSION DATE: | 26.07.2026
BUSINESS DATE: | 27.07.2026
1st ID CC Remedial Actions
Name of the RA | RA ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400 kV TINTARENI-KOZLODUI 1 | BG_RA_00001 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  |  |  | helpful
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful | helpful | helpful | helpful | helpful | notApplied | helpful |  |  |  | helpful | helpful | helpful | helpful | helpful | notApplied | notApplied | notApplied |  |  |  |  | notApplied
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00008 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  |  |  | notApplied
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00009 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  |  |  | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  |  | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  |  |  | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00017 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  |  |  | notApplied