## 0030Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 00:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3429
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1872 | 1920 | 1920 | -48 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1872 | 1920 | 1920 | -48 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1269 | 1570 | 1570 | -301 | 81 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1269 | 1570 | 1570 | -301 | 81 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1166 | 1570 | 1570 | -404 | 74 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1166 | 1570 | 1570 | -404 | 74 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1165 | 1570 | 1570 | -405 | 74 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1140 | 1570 | 1570 | -430 | 73 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1127 | 1570 | 1570 | -443 | 72 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1126 | 1570 | 1570 | -444 | 72 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1124 | 1570 | 1570 | -446 | 72 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1117 | 1570 | 1570 | -453 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1331 | 1890 | 1890 | -559 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1331 | 1890 | 1890 | -559 | 70 | []

## 0030Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 00:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3429
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1872 |  | 1920 | -48 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1872 |  | 1920 | -48 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1269 |  | 1570 | -301 | 81 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1269 |  | 1570 | -301 | 81 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1166 |  | 1570 | -404 | 74 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1166 |  | 1570 | -404 | 74 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1165 |  | 1570 | -405 | 74 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1140 |  | 1570 | -430 | 73 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1127 |  | 1570 | -443 | 72 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1126 |  | 1570 | -444 | 72 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1124 |  | 1570 | -446 | 72 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1117 |  | 1570 | -453 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1331 |  | 1890 | -559 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1331 |  | 1890 | -559 | 70 | []

## 0130Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 01:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3537
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1886 | 1890 | 1890 | -4 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1886 | 1890 | 1890 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1321 | 1570 | 1570 | -249 | 84 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1321 | 1570 | 1570 | -249 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1224 | 1570 | 1570 | -346 | 78 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1220 | 1570 | 1570 | -350 | 78 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1219 | 1570 | 1570 | -351 | 78 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1194 | 1570 | 1570 | -376 | 76 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1183 | 1570 | 1570 | -387 | 75 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1181 | 1570 | 1570 | -389 | 75 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1175 | 1570 | 1570 | -395 | 75 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1172 | 1570 | 1570 | -398 | 75 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1143 | 1570 | 1570 | -427 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1338 | 1890 | 1890 | -552 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1338 | 1890 | 1890 | -552 | 71 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1106 | 1570 | 1570 | -464 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1103 | 1570 | 1570 | -467 | 70 | []

## 0130Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 01:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3537
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1886 |  | 1890 | -4 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1886 |  | 1890 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 |  | 1920 | -49 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 |  | 1920 | -49 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1321 |  | 1570 | -249 | 84 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1321 |  | 1570 | -249 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1224 |  | 1570 | -346 | 78 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1220 |  | 1570 | -350 | 78 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1219 |  | 1570 | -351 | 78 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1194 |  | 1570 | -376 | 76 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1183 |  | 1570 | -387 | 75 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1181 |  | 1570 | -389 | 75 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1175 |  | 1570 | -395 | 75 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1172 |  | 1570 | -398 | 75 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1143 |  | 1570 | -427 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1338 |  | 1890 | -552 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1338 |  | 1890 | -552 | 71 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1106 |  | 1570 | -464 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1103 |  | 1570 | -467 | 70 | []

## 0230Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 02:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3596
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1885 | 1890 | 1890 | -5 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1885 | 1890 | 1890 | -5 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1870 | 1920 | 1920 | -50 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1870 | 1920 | 1920 | -50 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1265 | 1570 | 1570 | -305 | 81 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1265 | 1570 | 1570 | -305 | 81 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1174 | 1570 | 1570 | -396 | 75 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1173 | 1570 | 1570 | -397 | 75 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1169 | 1570 | 1570 | -401 | 74 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1140 | 1570 | 1570 | -430 | 73 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1129 | 1570 | 1570 | -441 | 72 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1126 | 1570 | 1570 | -444 | 72 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1118 | 1570 | 1570 | -452 | 71 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1116 | 1570 | 1570 | -454 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1330 | 1890 | 1890 | -560 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1330 | 1890 | 1890 | -560 | 70 | []

## 0230Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 02:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3596
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1885 |  | 1890 | -5 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1885 |  | 1890 | -5 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1870 |  | 1920 | -50 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1870 |  | 1920 | -50 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1265 |  | 1570 | -305 | 81 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1265 |  | 1570 | -305 | 81 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1174 |  | 1570 | -396 | 75 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1173 |  | 1570 | -397 | 75 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1169 |  | 1570 | -401 | 74 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1140 |  | 1570 | -430 | 73 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1129 |  | 1570 | -441 | 72 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1126 |  | 1570 | -444 | 72 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1118 |  | 1570 | -452 | 71 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1116 |  | 1570 | -454 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1330 |  | 1890 | -560 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1330 |  | 1890 | -560 | 70 | []

## 0330Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 03:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3737
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1886 | 1890 | 1890 | -4 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1886 | 1890 | 1890 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1367 | 1570 | 1570 | -203 | 87 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1367 | 1570 | 1570 | -203 | 87 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1288 | 1570 | 1570 | -282 | 82 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1285 | 1570 | 1570 | -285 | 82 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1284 | 1570 | 1570 | -286 | 82 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1251 | 1570 | 1570 | -319 | 80 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1240 | 1570 | 1570 | -330 | 79 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1235 | 1570 | 1570 | -335 | 79 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1222 | 1570 | 1570 | -348 | 78 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1221 | 1570 | 1570 | -349 | 78 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1203 | 1570 | 1570 | -367 | 77 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1160 | 1570 | 1570 | -410 | 74 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1153 | 1570 | 1570 | -417 | 73 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1118 | 1570 | 1570 | -452 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1345 | 1890 | 1890 | -545 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1345 | 1890 | 1890 | -545 | 71 | []

## 0330Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 03:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3737
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1886 |  | 1890 | -4 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1886 |  | 1890 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 |  | 1920 | -49 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 |  | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1367 |  | 1570 | -203 | 87 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1367 |  | 1570 | -203 | 87 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1288 |  | 1570 | -282 | 82 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1285 |  | 1570 | -285 | 82 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1284 |  | 1570 | -286 | 82 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1251 |  | 1570 | -319 | 80 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1240 |  | 1570 | -330 | 79 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1235 |  | 1570 | -335 | 79 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1222 |  | 1570 | -348 | 78 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1221 |  | 1570 | -349 | 78 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1203 |  | 1570 | -367 | 77 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1160 |  | 1570 | -410 | 74 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1153 |  | 1570 | -417 | 73 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1118 |  | 1570 | -452 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1345 |  | 1890 | -545 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1345 |  | 1890 | -545 | 71 | []

## 0430Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 04:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3814
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1874 | 1890 | 1890 | -16 | 99 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1874 | 1890 | 1890 | -16 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1858 | 1920 | 1920 | -62 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1858 | 1920 | 1920 | -62 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1411 | 1570 | 1570 | -159 | 90 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1411 | 1570 | 1570 | -159 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1333 | 1570 | 1570 | -237 | 85 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1332 | 1570 | 1570 | -238 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1332 | 1570 | 1570 | -238 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1296 | 1570 | 1570 | -274 | 83 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1285 | 1570 | 1570 | -285 | 82 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1281 | 1570 | 1570 | -289 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1268 | 1570 | 1570 | -302 | 81 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1266 | 1570 | 1570 | -304 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1249 | 1570 | 1570 | -321 | 80 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1205 | 1570 | 1570 | -365 | 77 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1200 | 1570 | 1570 | -370 | 76 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1163 | 1570 | 1570 | -407 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1344 | 1890 | 1890 | -546 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1344 | 1890 | 1890 | -546 | 71 | []

## 0430Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 04:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3814
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1874 |  | 1890 | -16 | 99 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1874 |  | 1890 | -16 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1858 |  | 1920 | -62 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1858 |  | 1920 | -62 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1411 |  | 1570 | -159 | 90 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1411 |  | 1570 | -159 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1333 |  | 1570 | -237 | 85 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1332 |  | 1570 | -238 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1332 |  | 1570 | -238 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1296 |  | 1570 | -274 | 83 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1285 |  | 1570 | -285 | 82 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1281 |  | 1570 | -289 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1268 |  | 1570 | -302 | 81 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1266 |  | 1570 | -304 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1249 |  | 1570 | -321 | 80 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1205 |  | 1570 | -365 | 77 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1200 |  | 1570 | -370 | 76 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1163 |  | 1570 | -407 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1344 |  | 1890 | -546 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1344 |  | 1890 | -546 | 71 | []

## 0530Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 05:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3832
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1846 | 1890 | 1890 | -44 | 98 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1846 | 1890 | 1890 | -44 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1830 | 1920 | 1920 | -90 | 95 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1830 | 1920 | 1920 | -90 | 95 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 | 1570 | 1570 | -168 | 89 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 | 1570 | 1570 | -168 | 89 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1332 | 1570 | 1570 | -238 | 85 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1331 | 1570 | 1570 | -239 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1321 | 1570 | 1570 | -249 | 84 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1290 | 1570 | 1570 | -280 | 82 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1277 | 1570 | 1570 | -293 | 81 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1273 | 1570 | 1570 | -297 | 81 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1260 | 1570 | 1570 | -310 | 80 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1258 | 1570 | 1570 | -312 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1239 | 1570 | 1570 | -331 | 79 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1197 | 1570 | 1570 | -373 | 76 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1189 | 1570 | 1570 | -381 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1169 | 1570 | 1570 | -401 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1326 | 1890 | 1890 | -564 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1326 | 1890 | 1890 | -564 | 70 | []

## 0530Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 05:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3832
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1846 |  | 1890 | -44 | 98 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1846 |  | 1890 | -44 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1830 |  | 1920 | -90 | 95 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1830 |  | 1920 | -90 | 95 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 |  | 1570 | -168 | 89 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 |  | 1570 | -168 | 89 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1332 |  | 1570 | -238 | 85 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1331 |  | 1570 | -239 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1321 |  | 1570 | -249 | 84 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1290 |  | 1570 | -280 | 82 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1277 |  | 1570 | -293 | 81 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1273 |  | 1570 | -297 | 81 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1260 |  | 1570 | -310 | 80 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1258 |  | 1570 | -312 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1239 |  | 1570 | -331 | 79 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1197 |  | 1570 | -373 | 76 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1189 |  | 1570 | -381 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1169 |  | 1570 | -401 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1326 |  | 1890 | -564 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1326 |  | 1890 | -564 | 70 | []

## 0630Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 06:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3544
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1886 | 1890 | 1890 | -4 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1886 | 1890 | 1890 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1872 | 1920 | 1920 | -48 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1872 | 1920 | 1920 | -48 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1166 | 1570 | 1570 | -404 | 74 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1166 | 1570 | 1570 | -404 | 74 | []

## 0630Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 06:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3544
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1886 |  | 1890 | -4 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1886 |  | 1890 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1872 |  | 1920 | -48 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1872 |  | 1920 | -48 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1166 |  | 1570 | -404 | 74 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1166 |  | 1570 | -404 | 74 | []

## 0730Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 07:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3790
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1886 | 1890 | 1890 | -4 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1886 | 1890 | 1890 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1872 | 1920 | 1920 | -48 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1872 | 1920 | 1920 | -48 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1617 | 2000 | 2000 | -383 | 81 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1612 | -2000 | -2000 | -388 | 81 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1601 | 2000 | 2000 | -399 | 80 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1595 | -2000 | -2000 | -405 | 80 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1194 | 1570 | 1570 | -376 | 76 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1194 | 1570 | 1570 | -376 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1370 | 1890 | 1890 | -520 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1370 | 1890 | 1890 | -520 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1361 | 1920 | 1920 | -559 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1361 | 1920 | 1920 | -559 | 71 | []

## 0730Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 07:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3790
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1886 |  | 1890 | -4 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1886 |  | 1890 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1872 |  | 1920 | -48 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1872 |  | 1920 | -48 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1617 |  | 2000 | -383 | 81 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1612 |  | -2000 | -388 | 81 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1601 |  | 2000 | -399 | 80 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1595 |  | -2000 | -405 | 80 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1194 |  | 1570 | -376 | 76 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1194 |  | 1570 | -376 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1370 |  | 1890 | -520 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1370 |  | 1890 | -520 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1361 |  | 1920 | -559 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1361 |  | 1920 | -559 | 71 | []

## 0830Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 08:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3681
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1872 | 1920 | 1920 | -48 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1872 | 1920 | 1920 | -48 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1686 | 2000 | 2000 | -314 | 84 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1680 | -2000 | -2000 | -320 | 84 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1669 | 2000 | 2000 | -331 | 83 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1663 | -2000 | -2000 | -337 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1339 | 1890 | 1890 | -551 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1339 | 1890 | 1890 | -551 | 71 | []

## 0830Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 08:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3681
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1872 |  | 1920 | -48 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1872 |  | 1920 | -48 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1686 |  | 2000 | -314 | 84 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1680 |  | -2000 | -320 | 84 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1669 |  | 2000 | -331 | 83 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1663 |  | -2000 | -337 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1339 |  | 1890 | -551 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1339 |  | 1890 | -551 | 71 | []

## 0930Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 09:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3612
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1885 | 1890 | 1890 | -5 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1885 | 1890 | 1890 | -5 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1655 | 2000 | 2000 | -345 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1649 | -2000 | -2000 | -351 | 82 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1638 | 2000 | 2000 | -362 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1632 | -2000 | -2000 | -368 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1327 | 1890 | 1890 | -563 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1327 | 1890 | 1890 | -563 | 70 | []

## 0930Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 09:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3612
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1885 |  | 1890 | -5 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1885 |  | 1890 | -5 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 |  | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 |  | 1920 | -49 | 97 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1655 |  | 2000 | -345 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1649 |  | -2000 | -351 | 82 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1638 |  | 2000 | -362 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1632 |  | -2000 | -368 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1327 |  | 1890 | -563 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1327 |  | 1890 | -563 | 70 | []

## 1030Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 10:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3709
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1806 | 1890 | 1890 | -84 | 96 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1806 | 1890 | 1890 | -84 | 96 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1792 | 1920 | 1920 | -128 | 93 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1792 | 1920 | 1920 | -128 | 93 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1651 | 2000 | 2000 | -349 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1645 | -2000 | -2000 | -355 | 82 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1634 | 2000 | 2000 | -366 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1628 | -2000 | -2000 | -372 | 81 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1215 | 1570 | 1570 | -355 | 77 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1215 | 1570 | 1570 | -355 | 77 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1135 | 1587 | 1587 | -452 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1328 | 1890 | 1890 | -562 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1328 | 1890 | 1890 | -562 | 70 | []

## 1030Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 10:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3709
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1806 |  | 1890 | -84 | 96 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1806 |  | 1890 | -84 | 96 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1792 |  | 1920 | -128 | 93 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1792 |  | 1920 | -128 | 93 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1651 |  | 2000 | -349 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1645 |  | -2000 | -355 | 82 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1634 |  | 2000 | -366 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1628 |  | -2000 | -372 | 81 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1215 |  | 1570 | -355 | 77 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1215 |  | 1570 | -355 | 77 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1135 |  | 1587 | -452 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1328 |  | 1890 | -562 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1328 |  | 1890 | -562 | 70 | []

## 1130Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 11:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3663
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 | 1570 | 1570 | -126 | 92 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 | 1570 | 1570 | -126 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1366 | 1570 | 1570 | -204 | 87 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1617 | 1890 | 1890 | -273 | 86 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1617 | 1890 | 1890 | -273 | 86 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1330 | 1570 | 1570 | -240 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1326 | 1570 | 1570 | -244 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1324 | 1570 | 1570 | -246 | 84 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1317 | 1570 | 1570 | -253 | 84 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1316 | 1570 | 1570 | -254 | 84 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1602 | 1920 | 1920 | -318 | 83 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1602 | 1920 | 1920 | -318 | 83 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1302 | 1570 | 1570 | -268 | 83 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1299 | 1570 | 1570 | -271 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1279 | 1570 | 1570 | -291 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1277 | 1570 | 1570 | -293 | 81 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1520 | 2000 | 2000 | -480 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1513 | -2000 | -2000 | -487 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1504 | 2000 | 2000 | -496 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1497 | -2000 | -2000 | -503 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1135 | 1570 | 1570 | -435 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1115 | 1570 | 1570 | -455 | 71 | []

## 1130Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 11:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3663
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 |  | 1570 | -126 | 92 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 |  | 1570 | -126 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1366 |  | 1570 | -204 | 87 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1617 |  | 1890 | -273 | 86 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1617 |  | 1890 | -273 | 86 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1330 |  | 1570 | -240 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1326 |  | 1570 | -244 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1324 |  | 1570 | -246 | 84 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1317 |  | 1570 | -253 | 84 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1316 |  | 1570 | -254 | 84 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1602 |  | 1920 | -318 | 83 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1602 |  | 1920 | -318 | 83 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1302 |  | 1570 | -268 | 83 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1299 |  | 1570 | -271 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1279 |  | 1570 | -291 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1277 |  | 1570 | -293 | 81 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1520 |  | 2000 | -480 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1513 |  | -2000 | -487 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1504 |  | 2000 | -496 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1497 |  | -2000 | -503 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1135 |  | 1570 | -435 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1115 |  | 1570 | -455 | 71 | []

## 1230Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 12:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3341
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1559 | 1570 | 1570 | -11 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1559 | 1570 | 1570 | -11 | 99 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1526 | 1570 | 1570 | -44 | 97 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1474 | 1570 | 1570 | -96 | 94 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1470 | 1570 | 1570 | -100 | 94 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1466 | 1570 | 1570 | -104 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1453 | 1570 | 1570 | -117 | 93 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 | 1570 | 1570 | -118 | 92 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1443 | 1570 | 1570 | -127 | 92 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 | 1570 | 1570 | -128 | 92 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1434 | 1570 | 1570 | -136 | 91 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1419 | 1570 | 1570 | -151 | 90 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1333 | 1570 | 1570 | -237 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1297 | 1570 | 1570 | -273 | 83 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1406 | 1890 | 1890 | -484 | 74 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1406 | 1890 | 1890 | -484 | 74 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1388 | 1920 | 1920 | -532 | 72 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1388 | 1920 | 1920 | -532 | 72 | []

## 1230Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 12:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3341
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1559 |  | 1570 | -11 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1559 |  | 1570 | -11 | 99 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1526 |  | 1570 | -44 | 97 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1474 |  | 1570 | -96 | 94 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1470 |  | 1570 | -100 | 94 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1466 |  | 1570 | -104 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1453 |  | 1570 | -117 | 93 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1570 | -118 | 92 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1443 |  | 1570 | -127 | 92 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 |  | 1570 | -128 | 92 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1434 |  | 1570 | -136 | 91 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1419 |  | 1570 | -151 | 90 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1333 |  | 1570 | -237 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1297 |  | 1570 | -273 | 83 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1406 |  | 1890 | -484 | 74 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1406 |  | 1890 | -484 | 74 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1388 |  | 1920 | -532 | 72 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1388 |  | 1920 | -532 | 72 | []

## 1330Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 13:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3534
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1564 | 1570 | 1570 | -6 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1564 | 1570 | 1570 | -6 | 100 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1514 | 1570 | 1570 | -56 | 96 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1464 | 1570 | 1570 | -106 | 93 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1464 | 1570 | 1570 | -106 | 93 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1458 | 1570 | 1570 | -112 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1445 | 1570 | 1570 | -125 | 92 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 | 1570 | 1570 | -126 | 92 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 | 1570 | 1570 | -135 | 91 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 | 1570 | 1570 | -143 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1418 | 1570 | 1570 | -152 | 90 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1409 | 1570 | 1570 | -161 | 90 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1293 | 1570 | 1570 | -277 | 82 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1528 | 1890 | 1890 | -362 | 81 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1528 | 1890 | 1890 | -362 | 81 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1264 | 1570 | 1570 | -306 | 81 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1512 | 1920 | 1920 | -408 | 79 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1512 | 1920 | 1920 | -408 | 79 | []

## 1330Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 13:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3534
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1564 |  | 1570 | -6 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1564 |  | 1570 | -6 | 100 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1514 |  | 1570 | -56 | 96 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1464 |  | 1570 | -106 | 93 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1464 |  | 1570 | -106 | 93 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1458 |  | 1570 | -112 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1445 |  | 1570 | -125 | 92 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 |  | 1570 | -126 | 92 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1570 | -135 | 91 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1570 | -143 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1418 |  | 1570 | -152 | 90 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1409 |  | 1570 | -161 | 90 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1293 |  | 1570 | -277 | 82 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1528 |  | 1890 | -362 | 81 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1528 |  | 1890 | -362 | 81 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1264 |  | 1570 | -306 | 81 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1512 |  | 1920 | -408 | 79 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1512 |  | 1920 | -408 | 79 | []

## 1430Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 14:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3729
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1737 | 1890 | 1890 | -153 | 92 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1737 | 1890 | 1890 | -153 | 92 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1416 | 1570 | 1570 | -154 | 90 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1416 | 1570 | 1570 | -154 | 90 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1721 | 1920 | 1920 | -199 | 90 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1721 | 1920 | 1920 | -199 | 90 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1325 | 1570 | 1570 | -245 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1290 | 1570 | 1570 | -280 | 82 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1290 | 1570 | 1570 | -280 | 82 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1286 | 1570 | 1570 | -284 | 82 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1277 | 1570 | 1570 | -293 | 81 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1276 | 1570 | 1570 | -294 | 81 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1264 | 1570 | 1570 | -306 | 81 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1261 | 1570 | 1570 | -309 | 80 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1595 | 2000 | 2000 | -405 | 80 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1585 | -2000 | -2000 | -415 | 79 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1240 | 1570 | 1570 | -330 | 79 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1578 | 2000 | 2000 | -422 | 79 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1568 | -2000 | -2000 | -432 | 78 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1231 | 1570 | 1570 | -339 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1330 | 1890 | 1890 | -560 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1330 | 1890 | 1890 | -560 | 70 | []

## 1430Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 14:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3729
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1737 |  | 1890 | -153 | 92 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1737 |  | 1890 | -153 | 92 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1416 |  | 1570 | -154 | 90 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1416 |  | 1570 | -154 | 90 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1721 |  | 1920 | -199 | 90 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1721 |  | 1920 | -199 | 90 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1325 |  | 1570 | -245 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1290 |  | 1570 | -280 | 82 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1290 |  | 1570 | -280 | 82 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1286 |  | 1570 | -284 | 82 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1277 |  | 1570 | -293 | 81 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1276 |  | 1570 | -294 | 81 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1264 |  | 1570 | -306 | 81 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1261 |  | 1570 | -309 | 80 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1595 |  | 2000 | -405 | 80 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1585 |  | -2000 | -415 | 79 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1240 |  | 1570 | -330 | 79 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1578 |  | 2000 | -422 | 79 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1568 |  | -2000 | -432 | 78 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1231 |  | 1570 | -339 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1330 |  | 1890 | -560 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1330 |  | 1890 | -560 | 70 | []

## 1530Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 15:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3165
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1886 | 1890 | 1890 | -4 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1886 | 1890 | 1890 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1872 | 1920 | 1920 | -48 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1872 | 1920 | 1920 | -48 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1506 | 2000 | 2000 | -494 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1496 | -2000 | -2000 | -504 | 75 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1490 | 2000 | 2000 | -510 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1479 | -2000 | -2000 | -521 | 74 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1112 | 1587 | 1587 | -475 | 70 | []

## 1530Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 15:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3165
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1886 |  | 1890 | -4 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1886 |  | 1890 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1872 |  | 1920 | -48 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1872 |  | 1920 | -48 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1506 |  | 2000 | -494 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1496 |  | -2000 | -504 | 75 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1490 |  | 2000 | -510 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1479 |  | -2000 | -521 | 74 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1112 |  | 1587 | -475 | 70 | []

## 1630Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 16:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3213
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1888 | 1890 | 1890 | -2 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1888 | 1890 | 1890 | -2 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1874 | 1920 | 1920 | -46 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1874 | 1920 | 1920 | -46 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1432 | 2000 | 2000 | -568 | 72 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1422 | -2000 | -2000 | -578 | 71 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1415 | 2000 | 2000 | -585 | 71 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1405 | -2000 | -2000 | -595 | 70 | []

## 1630Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 16:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3213
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1888 |  | 1890 | -2 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1888 |  | 1890 | -2 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1874 |  | 1920 | -46 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1874 |  | 1920 | -46 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1432 |  | 2000 | -568 | 72 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1422 |  | -2000 | -578 | 71 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1415 |  | 2000 | -585 | 71 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1405 |  | -2000 | -595 | 70 | []

## 1730Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 17:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3634
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1888 | 1890 | 1890 | -2 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1888 | 1890 | 1890 | -2 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1874 | 1920 | 1920 | -46 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1874 | 1920 | 1920 | -46 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1227 | 1570 | 1570 | -343 | 78 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1227 | 1570 | 1570 | -343 | 78 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1529 | 2000 | 2000 | -471 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1518 | -2000 | -2000 | -482 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1511 | 2000 | 2000 | -489 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1500 | -2000 | -2000 | -500 | 75 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1110 | 1570 | 1570 | -460 | 71 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1109 | 1570 | 1570 | -461 | 71 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1103 | 1570 | 1570 | -467 | 70 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1102 | 1570 | 1570 | -468 | 70 | []

## 1730Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 17:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3634
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1888 |  | 1890 | -2 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1888 |  | 1890 | -2 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1874 |  | 1920 | -46 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1874 |  | 1920 | -46 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1227 |  | 1570 | -343 | 78 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1227 |  | 1570 | -343 | 78 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1529 |  | 2000 | -471 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1518 |  | -2000 | -482 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1511 |  | 2000 | -489 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1500 |  | -2000 | -500 | 75 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1110 |  | 1570 | -460 | 71 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1109 |  | 1570 | -461 | 71 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1103 |  | 1570 | -467 | 70 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1102 |  | 1570 | -468 | 70 | []

## 1830Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 18:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3643
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1884 | 1890 | 1890 | -6 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1884 | 1890 | 1890 | -6 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1754 | 2000 | 2000 | -246 | 88 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1749 | -2000 | -2000 | -251 | 87 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1732 | 2000 | 2000 | -268 | 87 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1727 | -2000 | -2000 | -273 | 86 | []

## 1830Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 18:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3643
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1884 |  | 1890 | -6 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1884 |  | 1890 | -6 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 |  | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 |  | 1920 | -49 | 97 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1754 |  | 2000 | -246 | 88 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1749 |  | -2000 | -251 | 87 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1732 |  | 2000 | -268 | 87 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1727 |  | -2000 | -273 | 86 | []

## 1930Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 19:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3496
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1884 | 1890 | 1890 | -6 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1884 | 1890 | 1890 | -6 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1740 | 2000 | 2000 | -260 | 87 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1734 | -2000 | -2000 | -266 | 87 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1718 | 2000 | 2000 | -282 | 86 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1712 | -2000 | -2000 | -288 | 86 | []

## 1930Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 19:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3496
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1884 |  | 1890 | -6 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1884 |  | 1890 | -6 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 |  | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 |  | 1920 | -49 | 97 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1740 |  | 2000 | -260 | 87 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1734 |  | -2000 | -266 | 87 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1718 |  | 2000 | -282 | 86 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1712 |  | -2000 | -288 | 86 | []

## 2030Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 20:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3554
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1874 | 1920 | 1920 | -46 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1874 | 1920 | 1920 | -46 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1716 | 2000 | 2000 | -284 | 86 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1710 | -2000 | -2000 | -290 | 86 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1695 | 2000 | 2000 | -305 | 85 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1689 | -2000 | -2000 | -311 | 84 | []

## 2030Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 20:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3554
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1874 |  | 1920 | -46 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1874 |  | 1920 | -46 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1716 |  | 2000 | -284 | 86 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1710 |  | -2000 | -290 | 86 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1695 |  | 2000 | -305 | 85 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1689 |  | -2000 | -311 | 84 | []

## 2130Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 21:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3428
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1881 | 1890 | 1890 | -9 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1881 | 1890 | 1890 | -9 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1867 | 1920 | 1920 | -53 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1867 | 1920 | 1920 | -53 | 97 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1621 | 2000 | 2000 | -379 | 81 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1615 | -2000 | -2000 | -385 | 81 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1603 | 2000 | 2000 | -397 | 80 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1596 | -2000 | -2000 | -404 | 80 | []

## 2130Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 21:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3428
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1881 |  | 1890 | -9 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1881 |  | 1890 | -9 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1867 |  | 1920 | -53 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1867 |  | 1920 | -53 | 97 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1621 |  | 2000 | -379 | 81 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1615 |  | -2000 | -385 | 81 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1603 |  | 2000 | -397 | 80 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1596 |  | -2000 | -404 | 80 | []

## 2230Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 22:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3440
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1883 | 1890 | 1890 | -7 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1883 | 1890 | 1890 | -7 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1867 | 1920 | 1920 | -53 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1867 | 1920 | 1920 | -53 | 97 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1651 | 2000 | 2000 | -349 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1638 | -2000 | -2000 | -362 | 82 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1631 | 2000 | 2000 | -369 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1618 | -2000 | -2000 | -382 | 81 | []

## 2230Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 22:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3440
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1883 |  | 1890 | -7 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1883 |  | 1890 | -7 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1867 |  | 1920 | -53 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1867 |  | 1920 | -53 | 97 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1651 |  | 2000 | -349 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1638 |  | -2000 | -362 | 82 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1631 |  | 2000 | -369 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1618 |  | -2000 | -382 | 81 | []

## 2330Preventive
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 23:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3505
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1884 | 1890 | 1890 | -6 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1884 | 1890 | 1890 | -6 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1869 | 1920 | 1920 | -51 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1869 | 1920 | 1920 | -51 | 97 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1541 | 2000 | 2000 | -459 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1529 | -2000 | -2000 | -471 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1523 | 2000 | 2000 | -477 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1511 | -2000 | -2000 | -489 | 76 | []

## 2330Curative
Detailed results
Generated at: | 2026-07-29 20:02
Business day: | 30.07.2026
Timestamp: | 23:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3505
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1884 |  | 1890 | -6 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1884 |  | 1890 | -6 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1869 |  | 1920 | -51 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1869 |  | 1920 | -51 | 97 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1541 |  | 2000 | -459 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1529 |  | -2000 | -471 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1523 |  | 2000 | -477 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1511 |  | -2000 | -489 | 76 | []