## 1230Preventive
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 12:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3815
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1556 | 1587 | 1587 | -31 | 98 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1547 | 1600 | 1600 | -53 | 97 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1493 | 1587 | 1587 | -94 | 94 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1476 | 1600 | 1600 | -124 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1447 | 1587 | 1587 | -140 | 91 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1437 | 1587 | 1587 | -150 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1362 | 1587 | 1587 | -225 | 86 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1328 | 1587 | 1587 | -259 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1319 | 1587 | 1587 | -268 | 83 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1283 | 1587 | 1587 | -304 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 | 1587 | 1587 | -342 | 78 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1244 | 1587 | 1587 | -343 | 78 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1244 | 1587 | 1587 | -343 | 78 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1243 | 1587 | 1587 | -344 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 | 1600 | 1600 | -351 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1236 | 1587 | 1587 | -351 | 78 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1587 | 1587 | -384 | 76 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1587 | 1587 | -384 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 | 1587 | 1587 | -402 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 | 1587 | 1587 | -405 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 | 1587 | 1587 | -409 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 | 1587 | 1587 | -411 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 | 1587 | 1587 | -414 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 | 1587 | 1587 | -415 | 74 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 | 1587 | 1587 | -418 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 | 1587 | 1587 | -418 | 74 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 | 1587 | 1587 | -418 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1168 | 1587 | 1587 | -419 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1167 | 1587 | 1587 | -420 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1167 | 1587 | 1587 | -420 | 74 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1165 | 1587 | 1587 | -422 | 73 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1165 | 1587 | 1587 | -422 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1164 | 1587 | 1587 | -423 | 73 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1163 | 1587 | 1587 | -424 | 73 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1162 | 1587 | 1587 | -425 | 73 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1155 | 1587 | 1587 | -432 | 73 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1155 | 1587 | 1587 | -432 | 73 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1149 | 1587 | 1587 | -438 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 | 1587 | 1587 | -439 | 72 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 TIE 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1145 | 1587 | 1587 | -442 | 72 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 | 1587 | 1587 | -445 | 72 | []

## 1230Curative
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 12:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3815
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1556 |  | 1587 | -31 | 98 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1547 |  | 1600 | -53 | 97 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1493 |  | 1587 | -94 | 94 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1476 |  | 1600 | -124 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1447 |  | 1587 | -140 | 91 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1437 |  | 1587 | -150 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1362 |  | 1587 | -225 | 86 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1328 |  | 1587 | -259 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1319 |  | 1587 | -268 | 83 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1283 |  | 1587 | -304 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 |  | 1587 | -342 | 78 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1244 |  | 1587 | -343 | 78 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1244 |  | 1587 | -343 | 78 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1243 |  | 1587 | -344 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 |  | 1600 | -351 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1236 |  | 1587 | -351 | 78 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1231 |  | 1600 | -369 | 77 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1587 | -384 | 76 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1587 | -384 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 |  | 1587 | -402 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 |  | 1587 | -405 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 |  | 1587 | -409 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 |  | 1587 | -411 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 |  | 1587 | -414 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 |  | 1587 | -415 | 74 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 |  | 1587 | -418 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 |  | 1587 | -418 | 74 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 |  | 1587 | -418 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1168 |  | 1587 | -419 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1167 |  | 1587 | -420 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1167 |  | 1587 | -420 | 74 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1165 |  | 1587 | -422 | 73 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1165 |  | 1587 | -422 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1164 |  | 1587 | -423 | 73 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1163 |  | 1587 | -424 | 73 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1162 |  | 1587 | -425 | 73 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1155 |  | 1587 | -432 | 73 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1155 |  | 1587 | -432 | 73 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1149 |  | 1587 | -438 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 |  | 1587 | -439 | 72 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 TIE 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1145 |  | 1587 | -442 | 72 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 |  | 1587 | -445 | 72 | []

## 1330Preventive
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 13:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3787
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1582 | 1587 | 1587 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1530 | 1587 | 1587 | -57 | 96 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1533 | 1600 | 1600 | -67 | 96 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1474 | 1587 | 1587 | -113 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1462 | 1587 | 1587 | -125 | 92 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1470 | 1600 | 1600 | -130 | 92 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1393 | 1587 | 1587 | -194 | 88 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1362 | 1587 | 1587 | -225 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1345 | 1587 | 1587 | -242 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1319 | 1587 | 1587 | -268 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1282 | 1600 | 1600 | -318 | 80 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1272 | 1587 | 1587 | -315 | 80 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1271 | 1587 | 1587 | -316 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1270 | 1587 | 1587 | -317 | 80 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1266 | 1587 | 1587 | -321 | 80 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1266 | 1587 | 1587 | -321 | 80 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 | 1587 | 1587 | -350 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 | 1587 | 1587 | -355 | 78 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 | 1587 | 1587 | -358 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1587 | 1587 | -370 | 77 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 | 1587 | 1587 | -374 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1587 | 1587 | -376 | 76 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1587 | 1587 | -376 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 | 1587 | 1587 | -377 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 | 1587 | 1587 | -377 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1587 | 1587 | -383 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1587 | 1587 | -383 | 76 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1587 | 1587 | -384 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1587 | 1587 | -384 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 | 1587 | 1587 | -385 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 | 1587 | 1587 | -385 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 | 1587 | 1587 | -386 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 | 1587 | 1587 | -387 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1587 | 1587 | -389 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1587 | 1587 | -391 | 75 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1194 | 1587 | 1587 | -393 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 | 1587 | 1587 | -395 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 | 1587 | 1587 | -398 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 | 1587 | 1587 | -401 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 | 1587 | 1587 | -401 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 TIE 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 | 1587 | 1587 | -407 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 | 1587 | 1587 | -410 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1167 | 1587 | 1587 | -420 | 74 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1173 | 1600 | 1600 | -427 | 73 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 _XRO_MU11_1:line | -1272 | -1740 | -1740 | -468 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1155 | 1587 | 1587 | -432 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1150 | 1587 | 1587 | -437 | 72 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1122 | 1587 | 1587 | -465 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1120 | 1587 | 1587 | -467 | 71 | []

## 1330Curative
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 13:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3787
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1582 |  | 1587 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1530 |  | 1587 | -57 | 96 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1533 |  | 1600 | -67 | 96 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1474 |  | 1587 | -113 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1462 |  | 1587 | -125 | 92 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1470 |  | 1600 | -130 | 92 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1393 |  | 1587 | -194 | 88 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1362 |  | 1587 | -225 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1345 |  | 1587 | -242 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1319 |  | 1587 | -268 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1282 |  | 1600 | -318 | 80 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1272 |  | 1587 | -315 | 80 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1271 |  | 1587 | -316 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1270 |  | 1587 | -317 | 80 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1266 |  | 1587 | -321 | 80 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1266 |  | 1587 | -321 | 80 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 |  | 1587 | -350 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 |  | 1587 | -355 | 78 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 |  | 1587 | -358 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1587 | -370 | 77 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 |  | 1587 | -374 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1587 | -376 | 76 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1587 | -376 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 |  | 1587 | -377 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 |  | 1587 | -377 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1587 | -383 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1587 | -383 | 76 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1587 | -384 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1587 | -384 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 |  | 1587 | -385 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 |  | 1587 | -385 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 |  | 1587 | -386 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 |  | 1587 | -387 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1587 | -389 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1587 | -391 | 75 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1194 |  | 1587 | -393 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 |  | 1587 | -395 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 |  | 1587 | -398 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 |  | 1587 | -401 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 |  | 1587 | -401 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 TIE 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 |  | 1587 | -407 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 |  | 1587 | -410 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1167 |  | 1587 | -420 | 74 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1173 |  | 1600 | -427 | 73 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 _XRO_MU11_1:line | -1272 |  | -1740 | -468 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1155 |  | 1587 | -432 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1150 |  | 1587 | -437 | 72 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1122 |  | 1587 | -465 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1120 |  | 1587 | -467 | 71 | []

## 1430Preventive
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 14:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3749
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1586 | 1587 | 1587 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1544 | 1587 | 1587 | -43 | 97 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1489 | 1600 | 1600 | -111 | 93 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1476 | 1587 | 1587 | -111 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1463 | 1587 | 1587 | -124 | 92 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1434 | 1600 | 1600 | -166 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1379 | 1587 | 1587 | -208 | 87 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1366 | 1587 | 1587 | -221 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1343 | 1587 | 1587 | -244 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1306 | 1587 | 1587 | -281 | 82 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1293 | 1587 | 1587 | -294 | 81 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1292 | 1587 | 1587 | -295 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1274 | 1587 | 1587 | -313 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1283 | 1600 | 1600 | -317 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1272 | 1587 | 1587 | -315 | 80 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1269 | 1587 | 1587 | -318 | 80 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1247 | 1587 | 1587 | -340 | 79 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 | 1587 | 1587 | -343 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 | 1587 | 1587 | -355 | 78 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 | 1587 | 1587 | -369 | 77 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1587 | 1587 | -370 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 | 1587 | 1587 | -372 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 | 1587 | 1587 | -372 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 | 1587 | 1587 | -373 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 | 1587 | 1587 | -374 | 76 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1587 | 1587 | -380 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1587 | 1587 | -380 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1587 | 1587 | -380 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 | 1587 | 1587 | -381 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 | 1587 | 1587 | -381 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1587 | 1587 | -383 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1587 | 1587 | -383 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1587 | 1587 | -384 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 | 1587 | 1587 | -387 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1587 | 1587 | -388 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1587 | 1587 | -389 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 | 1587 | 1587 | -394 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 | 1587 | 1587 | -395 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 | 1587 | 1587 | -398 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 | 1587 | 1587 | -402 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 TIE 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1184 | 1587 | 1587 | -403 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 | 1587 | 1587 | -406 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 | 1587 | 1587 | -407 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 | 1587 | 1587 | -417 | 74 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 _XRO_MU11_1:line | -1275 | -1740 | -1740 | -465 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 | 1587 | 1587 | -427 | 73 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1137 | 1587 | 1587 | -450 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1145 | 1600 | 1600 | -455 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1129 | 1587 | 1587 | -458 | 71 | []

## 1430Curative
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 14:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3749
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1586 |  | 1587 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1544 |  | 1587 | -43 | 97 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1489 |  | 1600 | -111 | 93 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1476 |  | 1587 | -111 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1463 |  | 1587 | -124 | 92 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1434 |  | 1600 | -166 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1379 |  | 1587 | -208 | 87 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1366 |  | 1587 | -221 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1343 |  | 1587 | -244 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1306 |  | 1587 | -281 | 82 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1293 |  | 1587 | -294 | 81 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1292 |  | 1587 | -295 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1274 |  | 1587 | -313 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1283 |  | 1600 | -317 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1272 |  | 1587 | -315 | 80 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1269 |  | 1587 | -318 | 80 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1247 |  | 1587 | -340 | 79 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 |  | 1587 | -343 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 |  | 1587 | -355 | 78 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 |  | 1587 | -369 | 77 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1587 | -370 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 |  | 1587 | -372 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 |  | 1587 | -372 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 |  | 1587 | -373 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 |  | 1587 | -374 | 76 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1587 | -380 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1587 | -380 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1587 | -380 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 |  | 1587 | -381 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 |  | 1587 | -381 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1587 | -383 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1587 | -383 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1587 | -384 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 |  | 1587 | -387 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1587 | -388 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1587 | -389 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 |  | 1587 | -394 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 |  | 1587 | -395 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 |  | 1587 | -398 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 |  | 1587 | -402 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 TIE 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1184 |  | 1587 | -403 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 |  | 1587 | -406 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 |  | 1587 | -407 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 |  | 1587 | -417 | 74 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 _XRO_MU11_1:line | -1275 |  | -1740 | -465 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 |  | 1587 | -427 | 73 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1137 |  | 1587 | -450 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1145 |  | 1600 | -455 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1129 |  | 1587 | -458 | 71 | []

## 1530Preventive
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 15:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3443
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1582 | 1587 | 1587 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1563 | 1587 | 1587 | -24 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1468 | 1587 | 1587 | -119 | 92 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1465 | 1587 | 1587 | -122 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1444 | 1587 | 1587 | -143 | 91 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1379 | 1587 | 1587 | -208 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1368 | 1587 | 1587 | -219 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1337 | 1587 | 1587 | -250 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1315 | 1587 | 1587 | -272 | 83 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1315 | 1587 | 1587 | -272 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1274 | 1587 | 1587 | -313 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1269 | 1587 | 1587 | -318 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1276 | 1600 | 1600 | -324 | 80 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 | 1587 | 1587 | -326 | 79 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 | 1587 | 1587 | -336 | 79 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 | 1587 | 1587 | -342 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 | 1587 | 1587 | -346 | 78 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1235 | 1587 | 1587 | -352 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 | 1587 | 1587 | -359 | 77 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1225 | 1587 | 1587 | -362 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1223 | 1587 | 1587 | -364 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 | 1587 | 1587 | -365 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1587 | 1587 | -368 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1587 | 1587 | -370 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1587 | 1587 | -370 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1587 | 1587 | -370 | 77 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 | 1587 | 1587 | -371 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 | 1587 | 1587 | -372 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 | 1587 | 1587 | -373 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 | 1587 | 1587 | -373 | 77 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 | 1587 | 1587 | -373 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 | 1587 | 1587 | -374 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 | 1587 | 1587 | -377 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 | 1587 | 1587 | -377 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 | 1587 | 1587 | -378 | 76 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 | 1587 | 1587 | -378 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1587 | 1587 | -380 | 76 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1587 | 1587 | -383 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1587 | 1587 | -383 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1587 | 1587 | -388 | 76 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 | 1587 | 1587 | -395 | 75 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1200 | 1600 | 1600 | -400 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 | 1587 | 1587 | -409 | 74 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | -1183 | 1600 | 1600 | -417 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 | 1587 | 1587 | -417 | 74 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 | 1587 | 1587 | -436 | 73 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1128 | 1587 | 1587 | -459 | 71 | []

## 1530Curative
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 15:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3443
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1582 |  | 1587 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1563 |  | 1587 | -24 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1468 |  | 1587 | -119 | 92 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1465 |  | 1587 | -122 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1444 |  | 1587 | -143 | 91 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1379 |  | 1587 | -208 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1368 |  | 1587 | -219 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1337 |  | 1587 | -250 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1315 |  | 1587 | -272 | 83 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1315 |  | 1587 | -272 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1274 |  | 1587 | -313 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1269 |  | 1587 | -318 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1276 |  | 1600 | -324 | 80 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 |  | 1587 | -326 | 79 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 |  | 1587 | -336 | 79 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 |  | 1587 | -342 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 |  | 1587 | -346 | 78 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1235 |  | 1587 | -352 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 |  | 1587 | -359 | 77 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1225 |  | 1587 | -362 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1223 |  | 1587 | -364 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 |  | 1587 | -365 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1587 | -368 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1587 | -370 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1587 | -370 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1587 | -370 | 77 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 |  | 1587 | -371 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 |  | 1587 | -372 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 |  | 1587 | -373 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 |  | 1587 | -373 | 77 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 |  | 1587 | -373 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 |  | 1587 | -374 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 |  | 1587 | -377 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 |  | 1587 | -377 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 |  | 1587 | -378 | 76 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 |  | 1587 | -378 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1587 | -380 | 76 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1587 | -383 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1587 | -383 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1587 | -388 | 76 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 |  | 1587 | -395 | 75 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1200 |  | 1600 | -400 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 |  | 1587 | -409 | 74 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | -1183 |  | 1600 | -417 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 |  | 1587 | -417 | 74 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 |  | 1587 | -436 | 73 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1128 |  | 1587 | -459 | 71 | []

## 1630Preventive
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 16:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2819
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1584 | 1587 | 1587 | -3 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1558 | 1587 | 1587 | -29 | 98 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1481 | 1587 | 1587 | -106 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1472 | 1587 | 1587 | -115 | 93 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1377 | 1587 | 1587 | -210 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 | 1587 | 1587 | -249 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1336 | 1587 | 1587 | -251 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1309 | 1587 | 1587 | -278 | 82 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1309 | 1587 | 1587 | -278 | 82 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1300 | 1587 | 1587 | -287 | 82 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 | 1587 | 1587 | -339 | 79 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 | 1587 | 1587 | -342 | 78 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 | 1587 | 1587 | -343 | 78 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 | 1587 | 1587 | -343 | 78 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 | 1587 | 1587 | -353 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 | 1587 | 1587 | -356 | 78 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 | 1587 | 1587 | -358 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 | 1587 | 1587 | -359 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 | 1587 | 1587 | -359 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1226 | 1587 | 1587 | -361 | 77 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1225 | 1587 | 1587 | -362 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1587 | 1587 | -368 | 77 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1587 | 1587 | -368 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 | 1587 | 1587 | -369 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 | 1587 | 1587 | -369 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 | 1587 | 1587 | -369 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 | 1587 | 1587 | -369 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1587 | 1587 | -370 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 | 1587 | 1587 | -372 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 | 1587 | 1587 | -372 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 | 1587 | 1587 | -374 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1587 | 1587 | -375 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1587 | 1587 | -376 | 76 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1587 | 1587 | -376 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1587 | 1587 | -376 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 | 1587 | 1587 | -378 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 | 1587 | 1587 | -379 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 | 1587 | 1587 | -379 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 | 1587 | 1587 | -387 | 76 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1187 | 1587 | 1587 | -400 | 75 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 | 1587 | 1587 | -415 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1164 | 1587 | 1587 | -423 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 | 1587 | 1587 | -431 | 73 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1145 | 1587 | 1587 | -442 | 72 | []

## 1630Curative
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 16:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2819
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1584 |  | 1587 | -3 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1558 |  | 1587 | -29 | 98 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1481 |  | 1587 | -106 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1472 |  | 1587 | -115 | 93 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1377 |  | 1587 | -210 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 |  | 1587 | -249 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1336 |  | 1587 | -251 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1309 |  | 1587 | -278 | 82 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1309 |  | 1587 | -278 | 82 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1300 |  | 1587 | -287 | 82 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 |  | 1587 | -339 | 79 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 |  | 1600 | -345 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 |  | 1587 | -342 | 78 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 |  | 1587 | -343 | 78 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 |  | 1587 | -343 | 78 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 |  | 1587 | -353 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 |  | 1587 | -356 | 78 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 |  | 1587 | -358 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 |  | 1587 | -359 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 |  | 1587 | -359 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1226 |  | 1587 | -361 | 77 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1225 |  | 1587 | -362 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1587 | -368 | 77 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1587 | -368 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 |  | 1587 | -369 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 |  | 1587 | -369 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 |  | 1587 | -369 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 |  | 1587 | -369 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1587 | -370 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 |  | 1587 | -372 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 |  | 1587 | -372 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 |  | 1587 | -374 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1587 | -375 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1587 | -376 | 76 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1587 | -376 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1587 | -376 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 |  | 1587 | -378 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 |  | 1587 | -379 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 |  | 1587 | -379 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 |  | 1587 | -387 | 76 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1187 |  | 1587 | -400 | 75 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 |  | 1587 | -415 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1164 |  | 1587 | -423 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 |  | 1587 | -431 | 73 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1145 |  | 1587 | -442 | 72 | []

## 1730Preventive
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 17:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3298
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1585 | 1587 | 1587 | -2 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1581 | 1587 | 1587 | -6 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1467 | 1587 | 1587 | -120 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1434 | 1587 | 1587 | -153 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1408 | 1587 | 1587 | -179 | 89 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1385 | 1587 | 1587 | -202 | 87 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1365 | 1587 | 1587 | -222 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1328 | 1587 | 1587 | -259 | 84 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1328 | 1587 | 1587 | -259 | 84 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1325 | 1587 | 1587 | -262 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1291 | 1587 | 1587 | -296 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1300 | 1600 | 1600 | -300 | 81 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1279 | 1587 | 1587 | -308 | 81 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1262 | 1587 | 1587 | -325 | 79 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 | 1587 | 1587 | -326 | 79 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1252 | 1587 | 1587 | -335 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 | 1587 | 1587 | -336 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 | 1587 | 1587 | -338 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 | 1587 | 1587 | -346 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 | 1587 | 1587 | -348 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1238 | 1587 | 1587 | -349 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1238 | 1587 | 1587 | -349 | 78 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1238 | 1587 | 1587 | -349 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 | 1587 | 1587 | -350 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 | 1587 | 1587 | -354 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 | 1587 | 1587 | -354 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 | 1587 | 1587 | -355 | 78 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 | 1587 | 1587 | -356 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 | 1587 | 1587 | -356 | 78 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 | 1587 | 1587 | -356 | 78 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1230 | 1587 | 1587 | -357 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 | 1587 | 1587 | -358 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 | 1587 | 1587 | -359 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1224 | 1587 | 1587 | -363 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1224 | 1587 | 1587 | -363 | 77 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 TIE 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1223 | 1587 | 1587 | -364 | 77 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1587 | 1587 | -368 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1587 | 1587 | -368 | 77 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1587 | 1587 | -368 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 | 1587 | 1587 | -372 | 77 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 | 1587 | 1587 | -377 | 76 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1587 | 1587 | -384 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1587 | 1587 | -391 | 75 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 | 1587 | 1587 | -439 | 72 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 | 1587 | 1587 | -461 | 71 | []

## 1730Curative
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 17:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3298
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1585 |  | 1587 | -2 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1581 |  | 1587 | -6 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1467 |  | 1587 | -120 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1434 |  | 1587 | -153 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1408 |  | 1587 | -179 | 89 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1385 |  | 1587 | -202 | 87 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1365 |  | 1587 | -222 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1328 |  | 1587 | -259 | 84 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1328 |  | 1587 | -259 | 84 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1325 |  | 1587 | -262 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1291 |  | 1587 | -296 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1300 |  | 1600 | -300 | 81 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1279 |  | 1587 | -308 | 81 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1262 |  | 1587 | -325 | 79 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 |  | 1587 | -326 | 79 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1252 |  | 1587 | -335 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 |  | 1587 | -336 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 |  | 1587 | -338 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 |  | 1587 | -346 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 |  | 1587 | -348 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1238 |  | 1587 | -349 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1238 |  | 1587 | -349 | 78 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1238 |  | 1587 | -349 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 |  | 1587 | -350 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 |  | 1587 | -354 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 |  | 1587 | -354 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 |  | 1587 | -355 | 78 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 |  | 1587 | -356 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 |  | 1587 | -356 | 78 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 |  | 1587 | -356 | 78 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1230 |  | 1587 | -357 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 |  | 1587 | -358 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 |  | 1587 | -359 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1224 |  | 1587 | -363 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1224 |  | 1587 | -363 | 77 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 TIE 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1223 |  | 1587 | -364 | 77 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1587 | -368 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1587 | -368 | 77 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1587 | -368 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 |  | 1587 | -372 | 77 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 |  | 1587 | -377 | 76 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1587 | -384 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1587 | -391 | 75 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 |  | 1587 | -439 | 72 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 |  | 1587 | -461 | 71 | []

## 1830Preventive
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 18:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3118
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1586 | 1587 | 1587 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1535 | 1587 | 1587 | -52 | 97 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1454 | 1587 | 1587 | -133 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1342 | 1587 | 1587 | -245 | 85 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1322 | 1587 | 1587 | -265 | 83 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1321 | 1587 | 1587 | -266 | 83 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1320 | 1587 | 1587 | -267 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1290 | 1587 | 1587 | -297 | 81 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 | 1587 | 1587 | -310 | 80 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 | 1587 | 1587 | -353 | 78 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 | 1587 | 1587 | -353 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1587 | 1587 | -375 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1587 | 1587 | -375 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1587 | 1587 | -390 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1587 | 1587 | -391 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 TIE 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1194 | 1587 | 1587 | -393 | 75 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 | 1587 | 1587 | -401 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 | 1587 | 1587 | -404 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 | 1587 | 1587 | -404 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 | 1587 | 1587 | -404 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 | 1587 | 1587 | -404 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 | 1587 | 1587 | -406 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 | 1587 | 1587 | -407 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 | 1587 | 1587 | -409 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 | 1587 | 1587 | -411 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 | 1587 | 1587 | -411 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 | 1587 | 1587 | -413 | 74 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 | 1587 | 1587 | -413 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 | 1587 | 1587 | -414 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 | 1587 | 1587 | -414 | 74 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 | 1587 | 1587 | -417 | 74 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1169 | 1587 | 1587 | -418 | 74 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1169 | 1587 | 1587 | -418 | 74 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 | 1587 | 1587 | -427 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 | 1587 | 1587 | -427 | 73 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 | 1587 | 1587 | -439 | 72 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1140 | 1587 | 1587 | -447 | 72 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1128 | 1587 | 1587 | -459 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 18:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3118
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1586 |  | 1587 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1535 |  | 1587 | -52 | 97 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1454 |  | 1587 | -133 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1342 |  | 1587 | -245 | 85 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1322 |  | 1587 | -265 | 83 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1321 |  | 1587 | -266 | 83 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1320 |  | 1587 | -267 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1290 |  | 1587 | -297 | 81 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 |  | 1587 | -310 | 80 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 |  | 1587 | -353 | 78 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 |  | 1587 | -353 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1587 | -375 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1587 | -375 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1587 | -390 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1587 | -391 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 TIE 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1194 |  | 1587 | -393 | 75 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 |  | 1587 | -401 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 |  | 1587 | -404 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 |  | 1587 | -404 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 |  | 1587 | -404 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 |  | 1587 | -404 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 |  | 1587 | -406 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 |  | 1587 | -407 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 |  | 1587 | -409 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 |  | 1587 | -411 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 |  | 1587 | -411 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 |  | 1587 | -413 | 74 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 |  | 1587 | -413 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 |  | 1587 | -414 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 |  | 1587 | -414 | 74 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 |  | 1587 | -417 | 74 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1169 |  | 1587 | -418 | 74 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1169 |  | 1587 | -418 | 74 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 |  | 1587 | -427 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 |  | 1587 | -427 | 73 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 |  | 1587 | -439 | 72 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1140 |  | 1587 | -447 | 72 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1128 |  | 1587 | -459 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 19:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3131
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1582 | 1587 | 1587 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1513 | 1587 | 1587 | -74 | 95 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1432 | 1587 | 1587 | -155 | 90 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1349 | 1587 | 1587 | -238 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1349 | 1587 | 1587 | -238 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1278 | 1587 | 1587 | -309 | 81 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1253 | 1587 | 1587 | -334 | 79 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1251 | 1587 | 1587 | -336 | 79 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1251 | 1587 | 1587 | -336 | 79 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 | 1587 | 1587 | -348 | 78 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 | 1587 | 1587 | -366 | 77 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 | 1587 | 1587 | -399 | 75 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 | 1587 | 1587 | -407 | 74 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 | 1587 | 1587 | -408 | 74 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 | 1587 | 1587 | -414 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1172 | 1587 | 1587 | -415 | 74 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 | 1587 | 1587 | -421 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 | 1600 | 1600 | -426 | 73 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1161 | 1587 | 1587 | -426 | 73 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1158 | 1587 | 1587 | -429 | 73 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 | 1587 | 1587 | -431 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1155 | 1587 | 1587 | -432 | 73 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1154 | 1587 | 1587 | -433 | 73 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1150 | 1587 | 1587 | -437 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1148 | 1587 | 1587 | -439 | 72 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1147 | 1587 | 1587 | -440 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1144 | 1587 | 1587 | -443 | 72 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1139 | 1587 | 1587 | -448 | 72 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1133 | 1587 | 1587 | -454 | 71 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 | 1587 | 1587 | -455 | 71 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 | 1587 | 1587 | -455 | 71 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1131 | 1587 | 1587 | -456 | 71 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1130 | 1587 | 1587 | -457 | 71 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1129 | 1587 | 1587 | -458 | 71 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1128 | 1587 | 1587 | -459 | 71 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 | 1587 | 1587 | -461 | 71 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 | 1587 | 1587 | -461 | 71 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 | 1587 | 1587 | -461 | 71 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1125 | 1587 | 1587 | -462 | 71 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1123 | 1587 | 1587 | -464 | 71 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1123 | 1587 | 1587 | -464 | 71 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1123 | 1587 | 1587 | -464 | 71 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1121 | 1587 | 1587 | -466 | 71 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1120 | 1587 | 1587 | -467 | 71 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1120 | 1587 | 1587 | -467 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1115 | 1587 | 1587 | -472 | 70 | []

## 1930Curative
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 19:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3131
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1582 |  | 1587 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1513 |  | 1587 | -74 | 95 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1432 |  | 1587 | -155 | 90 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1349 |  | 1587 | -238 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1349 |  | 1587 | -238 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1278 |  | 1587 | -309 | 81 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1253 |  | 1587 | -334 | 79 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1251 |  | 1587 | -336 | 79 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1251 |  | 1587 | -336 | 79 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 |  | 1587 | -348 | 78 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 |  | 1587 | -366 | 77 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 |  | 1587 | -399 | 75 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 |  | 1587 | -407 | 74 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 |  | 1587 | -408 | 74 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 |  | 1587 | -414 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1172 |  | 1587 | -415 | 74 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 |  | 1587 | -421 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 |  | 1600 | -426 | 73 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1161 |  | 1587 | -426 | 73 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1158 |  | 1587 | -429 | 73 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 |  | 1587 | -431 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1155 |  | 1587 | -432 | 73 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1154 |  | 1587 | -433 | 73 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1150 |  | 1587 | -437 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1148 |  | 1587 | -439 | 72 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1147 |  | 1587 | -440 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1144 |  | 1587 | -443 | 72 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1139 |  | 1587 | -448 | 72 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1133 |  | 1587 | -454 | 71 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 |  | 1587 | -455 | 71 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 |  | 1587 | -455 | 71 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1131 |  | 1587 | -456 | 71 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1130 |  | 1587 | -457 | 71 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1129 |  | 1587 | -458 | 71 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1128 |  | 1587 | -459 | 71 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 |  | 1587 | -461 | 71 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 |  | 1587 | -461 | 71 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 |  | 1587 | -461 | 71 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1125 |  | 1587 | -462 | 71 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1123 |  | 1587 | -464 | 71 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1123 |  | 1587 | -464 | 71 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1123 |  | 1587 | -464 | 71 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1121 |  | 1587 | -466 | 71 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1120 |  | 1587 | -467 | 71 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1120 |  | 1587 | -467 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1115 |  | 1587 | -472 | 70 | []

## 2030Preventive
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 20:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3109
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1580 | 1587 | 1587 | -7 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1468 | 1587 | 1587 | -119 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1420 | 1587 | 1587 | -167 | 89 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1334 | 1587 | 1587 | -253 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1327 | 1587 | 1587 | -260 | 84 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1327 | 1587 | 1587 | -260 | 84 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1311 | 1587 | 1587 | -276 | 83 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1311 | 1587 | 1587 | -276 | 83 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1247 | 1587 | 1587 | -340 | 79 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1238 | 1587 | 1587 | -349 | 78 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 | 1587 | 1587 | -356 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1222 | 1587 | 1587 | -365 | 77 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1211 | 1587 | 1587 | -376 | 76 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1195 | 1587 | 1587 | -392 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 | 1587 | 1587 | -396 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1179 | 1587 | 1587 | -408 | 74 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 | 1587 | 1587 | -414 | 74 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1162 | 1587 | 1587 | -425 | 73 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1156 | 1587 | 1587 | -431 | 73 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 | 1587 | 1587 | -431 | 73 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1154 | 1587 | 1587 | -433 | 73 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1154 | 1587 | 1587 | -433 | 73 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1139 | 1587 | 1587 | -448 | 72 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1137 | 1587 | 1587 | -450 | 72 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1131 | 1587 | 1587 | -456 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1131 | 1587 | 1587 | -456 | 71 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1128 | 1587 | 1587 | -459 | 71 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1128 | 1587 | 1587 | -459 | 71 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1127 | 1587 | 1587 | -460 | 71 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 | 1587 | 1587 | -461 | 71 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1125 | 1587 | 1587 | -462 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1124 | 1587 | 1587 | -463 | 71 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1123 | 1587 | 1587 | -464 | 71 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1131 | 1600 | 1600 | -469 | 71 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1121 | 1587 | 1587 | -466 | 71 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1121 | 1587 | 1587 | -466 | 71 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1119 | 1587 | 1587 | -468 | 71 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1119 | 1587 | 1587 | -468 | 71 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1119 | 1587 | 1587 | -468 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1118 | 1587 | 1587 | -469 | 70 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1116 | 1587 | 1587 | -471 | 70 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1116 | 1587 | 1587 | -471 | 70 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1114 | 1587 | 1587 | -473 | 70 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1114 | 1587 | 1587 | -473 | 70 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1113 | 1587 | 1587 | -474 | 70 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1112 | 1587 | 1587 | -475 | 70 | []

## 2030Curative
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 20:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3109
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1580 |  | 1587 | -7 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1468 |  | 1587 | -119 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1420 |  | 1587 | -167 | 89 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1334 |  | 1587 | -253 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1327 |  | 1587 | -260 | 84 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1327 |  | 1587 | -260 | 84 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1311 |  | 1587 | -276 | 83 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1311 |  | 1587 | -276 | 83 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1247 |  | 1587 | -340 | 79 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1238 |  | 1587 | -349 | 78 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 |  | 1587 | -356 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1222 |  | 1587 | -365 | 77 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1211 |  | 1587 | -376 | 76 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1195 |  | 1587 | -392 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 |  | 1587 | -396 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1179 |  | 1587 | -408 | 74 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 |  | 1587 | -414 | 74 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1162 |  | 1587 | -425 | 73 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1156 |  | 1587 | -431 | 73 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 |  | 1587 | -431 | 73 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1154 |  | 1587 | -433 | 73 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1154 |  | 1587 | -433 | 73 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1139 |  | 1587 | -448 | 72 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1137 |  | 1587 | -450 | 72 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1131 |  | 1587 | -456 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1131 |  | 1587 | -456 | 71 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1140 |  | 1600 | -460 | 71 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1128 |  | 1587 | -459 | 71 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1128 |  | 1587 | -459 | 71 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1127 |  | 1587 | -460 | 71 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 |  | 1587 | -461 | 71 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1125 |  | 1587 | -462 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1124 |  | 1587 | -463 | 71 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1123 |  | 1587 | -464 | 71 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1131 |  | 1600 | -469 | 71 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1121 |  | 1587 | -466 | 71 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1121 |  | 1587 | -466 | 71 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1119 |  | 1587 | -468 | 71 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1119 |  | 1587 | -468 | 71 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1119 |  | 1587 | -468 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1118 |  | 1587 | -469 | 70 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1116 |  | 1587 | -471 | 70 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1116 |  | 1587 | -471 | 70 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1114 |  | 1587 | -473 | 70 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1114 |  | 1587 | -473 | 70 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1113 |  | 1587 | -474 | 70 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1112 |  | 1587 | -475 | 70 | []

## 2130Preventive
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 21:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3204
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1581 | 1587 | 1587 | -6 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1486 | 1587 | 1587 | -101 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1426 | 1587 | 1587 | -161 | 90 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1343 | 1587 | 1587 | -244 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1343 | 1587 | 1587 | -244 | 85 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1303 | 1587 | 1587 | -284 | 82 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1289 | 1587 | 1587 | -298 | 81 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1289 | 1587 | 1587 | -298 | 81 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 | 1587 | 1587 | -333 | 79 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1237 | 1587 | 1587 | -350 | 78 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1209 | 1587 | 1587 | -378 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1587 | 1587 | -383 | 76 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 | 1587 | 1587 | -385 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1197 | 1587 | 1587 | -390 | 75 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1194 | 1587 | 1587 | -393 | 75 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 | 1587 | 1587 | -410 | 74 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1173 | 1587 | 1587 | -414 | 74 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1160 | 1587 | 1587 | -427 | 73 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1149 | 1587 | 1587 | -438 | 72 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 | 1587 | 1587 | -439 | 72 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1148 | 1587 | 1587 | -439 | 72 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1141 | 1587 | 1587 | -446 | 72 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 | 1600 | 1600 | -449 | 72 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1140 | 1587 | 1587 | -447 | 72 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 | 1587 | 1587 | -455 | 71 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1130 | 1587 | 1587 | -457 | 71 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1122 | 1587 | 1587 | -465 | 71 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1121 | 1587 | 1587 | -466 | 71 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1120 | 1587 | 1587 | -467 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1119 | 1587 | 1587 | -468 | 70 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1118 | 1587 | 1587 | -469 | 70 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1118 | 1587 | 1587 | -469 | 70 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1117 | 1587 | 1587 | -470 | 70 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1126 | 1600 | 1600 | -474 | 70 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1113 | 1587 | 1587 | -474 | 70 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1113 | 1587 | 1587 | -474 | 70 | []

## 2130Curative
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 21:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3204
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1581 |  | 1587 | -6 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1486 |  | 1587 | -101 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1426 |  | 1587 | -161 | 90 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1343 |  | 1587 | -244 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1343 |  | 1587 | -244 | 85 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1303 |  | 1587 | -284 | 82 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1289 |  | 1587 | -298 | 81 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1289 |  | 1587 | -298 | 81 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 |  | 1587 | -333 | 79 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1237 |  | 1587 | -350 | 78 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1209 |  | 1587 | -378 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1587 | -383 | 76 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 |  | 1587 | -385 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1197 |  | 1587 | -390 | 75 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1194 |  | 1587 | -393 | 75 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 |  | 1587 | -410 | 74 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1173 |  | 1587 | -414 | 74 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1160 |  | 1587 | -427 | 73 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1149 |  | 1587 | -438 | 72 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 |  | 1587 | -439 | 72 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1148 |  | 1587 | -439 | 72 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1141 |  | 1587 | -446 | 72 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 |  | 1600 | -449 | 72 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1140 |  | 1587 | -447 | 72 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 |  | 1587 | -455 | 71 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1130 |  | 1587 | -457 | 71 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1122 |  | 1587 | -465 | 71 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1121 |  | 1587 | -466 | 71 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1120 |  | 1587 | -467 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1119 |  | 1587 | -468 | 70 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1118 |  | 1587 | -469 | 70 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1118 |  | 1587 | -469 | 70 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1117 |  | 1587 | -470 | 70 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1126 |  | 1600 | -474 | 70 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1113 |  | 1587 | -474 | 70 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Ptolemaida / N-1 OHL 400 kV Kardia - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1113 |  | 1587 | -474 | 70 | []

## 2230Preventive
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 22:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3395
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1583 | 1587 | 1587 | -4 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1508 | 1587 | 1587 | -79 | 95 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1432 | 1587 | 1587 | -155 | 90 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1363 | 1587 | 1587 | -224 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1362 | 1587 | 1587 | -225 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 | 1587 | 1587 | -300 | 81 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1262 | 1587 | 1587 | -325 | 79 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1256 | 1587 | 1587 | -331 | 79 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1256 | 1587 | 1587 | -331 | 79 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 | 1587 | 1587 | -350 | 78 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1208 | 1587 | 1587 | -379 | 76 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 | 1587 | 1587 | -386 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 | 1587 | 1587 | -413 | 74 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1171 | 1587 | 1587 | -416 | 74 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 | 1600 | 1600 | -420 | 74 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1170 | 1587 | 1587 | -417 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1167 | 1587 | 1587 | -420 | 74 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1158 | 1587 | 1587 | -429 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1154 | 1587 | 1587 | -433 | 73 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1138 | 1587 | 1587 | -449 | 72 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1138 | 1587 | 1587 | -449 | 72 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1137 | 1587 | 1587 | -450 | 72 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1136 | 1587 | 1587 | -451 | 72 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1133 | 1587 | 1587 | -454 | 71 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1125 | 1587 | 1587 | -462 | 71 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1124 | 1587 | 1587 | -463 | 71 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1123 | 1587 | 1587 | -464 | 71 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1119 | 1587 | 1587 | -468 | 70 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1118 | 1587 | 1587 | -469 | 70 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1118 | 1587 | 1587 | -469 | 70 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1115 | 1587 | 1587 | -472 | 70 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1112 | 1587 | 1587 | -475 | 70 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1111 | 1587 | 1587 | -476 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 22:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3395
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1583 |  | 1587 | -4 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1508 |  | 1587 | -79 | 95 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1432 |  | 1587 | -155 | 90 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1363 |  | 1587 | -224 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1362 |  | 1587 | -225 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 |  | 1587 | -300 | 81 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1262 |  | 1587 | -325 | 79 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1256 |  | 1587 | -331 | 79 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1256 |  | 1587 | -331 | 79 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 |  | 1587 | -350 | 78 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1208 |  | 1587 | -379 | 76 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 |  | 1587 | -386 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 |  | 1587 | -413 | 74 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1171 |  | 1587 | -416 | 74 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 |  | 1600 | -420 | 74 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1170 |  | 1587 | -417 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1167 |  | 1587 | -420 | 74 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1158 |  | 1587 | -429 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1154 |  | 1587 | -433 | 73 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1138 |  | 1587 | -449 | 72 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1138 |  | 1587 | -449 | 72 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1137 |  | 1587 | -450 | 72 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1136 |  | 1587 | -451 | 72 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1133 |  | 1587 | -454 | 71 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1125 |  | 1587 | -462 | 71 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1124 |  | 1587 | -463 | 71 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1123 |  | 1587 | -464 | 71 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1119 |  | 1587 | -468 | 70 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1118 |  | 1587 | -469 | 70 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1118 |  | 1587 | -469 | 70 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1115 |  | 1587 | -472 | 70 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1112 |  | 1587 | -475 | 70 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1111 |  | 1587 | -476 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 23:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3533
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1582 | 1587 | 1587 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1534 | 1587 | 1587 | -53 | 97 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1441 | 1587 | 1587 | -146 | 91 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1382 | 1587 | 1587 | -205 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1382 | 1587 | 1587 | -205 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1327 | 1587 | 1587 | -260 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1274 | 1587 | 1587 | -313 | 80 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 | 1587 | 1587 | -348 | 78 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1587 | 1587 | -370 | 77 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1210 | 1587 | 1587 | -377 | 76 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1210 | 1587 | 1587 | -377 | 76 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1587 | 1587 | -382 | 76 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 | 1600 | 1600 | -386 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1201 | 1587 | 1587 | -386 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 | 1587 | 1587 | -392 | 75 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 | 1587 | 1587 | -409 | 74 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1168 | 1587 | 1587 | -419 | 74 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1164 | 1587 | 1587 | -423 | 73 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 | 1587 | 1587 | -427 | 73 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1153 | 1587 | 1587 | -434 | 73 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1150 | 1587 | 1587 | -437 | 72 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 | 1587 | 1587 | -439 | 72 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 | 1587 | 1587 | -445 | 72 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 | 1587 | 1587 | -445 | 72 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1141 | 1587 | 1587 | -446 | 72 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1140 | 1587 | 1587 | -447 | 72 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 | 1587 | 1587 | -453 | 71 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 | 1587 | 1587 | -453 | 71 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 | 1587 | 1587 | -453 | 71 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 | 1587 | 1587 | -455 | 71 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1132 | 1587 | 1587 | -455 | 71 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 | 1587 | 1587 | -455 | 71 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1131 | 1587 | 1587 | -456 | 71 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1130 | 1587 | 1587 | -457 | 71 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1128 | 1587 | 1587 | -459 | 71 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 | 1587 | 1587 | -461 | 71 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 | 1587 | 1587 | -461 | 71 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 | 1587 | 1587 | -461 | 71 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1125 | 1587 | 1587 | -462 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1122 | 1587 | 1587 | -465 | 71 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1122 | 1587 | 1587 | -465 | 71 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1117 | 1587 | 1587 | -470 | 70 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1112 | 1587 | 1587 | -475 | 70 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1112 | 1587 | 1587 | -475 | 70 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1112 | 1587 | 1587 | -475 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2026-08-22 08:29
Business day: | 22.08.2026
Timestamp: | 23:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3533
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1582 |  | 1587 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1534 |  | 1587 | -53 | 97 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 3 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1441 |  | 1587 | -146 | 91 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1382 |  | 1587 | -205 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1382 |  | 1587 | -205 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1327 |  | 1587 | -260 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1274 |  | 1587 | -313 | 80 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 |  | 1587 | -348 | 78 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1587 | -370 | 77 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1210 |  | 1587 | -377 | 76 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1210 |  | 1587 | -377 | 76 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1587 | -382 | 76 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 |  | 1600 | -386 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1201 |  | 1587 | -386 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 |  | 1587 | -392 | 75 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 3 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 |  | 1587 | -409 | 74 | []
GR_CO_00010 | N-1 OHL 400 kV Amideo - Ptolemaida / N-1 OHL 400 kV Amideo - Vermio | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1168 |  | 1587 | -419 | 74 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1164 |  | 1587 | -423 | 73 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 |  | 1587 | -427 | 73 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1153 |  | 1587 | -434 | 73 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1150 |  | 1587 | -437 | 72 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 |  | 1587 | -439 | 72 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 |  | 1587 | -445 | 72 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 |  | 1587 | -445 | 72 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1141 |  | 1587 | -446 | 72 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1140 |  | 1587 | -447 | 72 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1147 |  | 1600 | -453 | 72 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 |  | 1587 | -453 | 71 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 |  | 1587 | -453 | 71 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 |  | 1587 | -453 | 71 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 |  | 1587 | -455 | 71 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1132 |  | 1587 | -455 | 71 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 |  | 1587 | -455 | 71 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1131 |  | 1587 | -456 | 71 | []
GR_CO_00009 | N-1 OHL 400 kV Filippoi - Lagadas ck. 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1130 |  | 1587 | -457 | 71 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1128 |  | 1587 | -459 | 71 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 |  | 1587 | -461 | 71 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 |  | 1587 | -461 | 71 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 |  | 1587 | -461 | 71 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1125 |  | 1587 | -462 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1122 |  | 1587 | -465 | 71 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1122 |  | 1587 | -465 | 71 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1117 |  | 1587 | -470 | 70 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1112 |  | 1587 | -475 | 70 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1112 |  | 1587 | -475 | 70 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1112 |  | 1587 | -475 | 70 | []