## SRO borders-exports
SUBMISSION DATE: | 21.08.2026
BUSINESS DATE: | 23.08.2026
DA CC Remedial Actions
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC RO-BG
00:00 | 01:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 4068 | 3868 | 2708
01:00 | 02:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 4177 | 3977 | 2784
02:00 | 03:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3831 | 3631 | 2542
03:00 | 04:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 93 | 3784 | 3584 | 2509
04:00 | 05:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 97 | 3785 | 3585 | 2510
05:00 | 06:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 98 | 3823 | 3623 | 2536
06:00 | 07:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 97 | 3828 | 3628 | 2540
07:00 | 08:00 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 2966 | 2766 | 1936
08:00 | 09:00 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 101 | 1508 | 1308 | 916
09:00 | 10:00 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 101 | 1202 | 1002 | 701
10:00 | 11:00 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 101 | 2209 | 2009 | 1406
11:00 | 12:00 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3733 | 3533 | 2473
12:00 | 13:00 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 100 | 4011 | 3811 | 2668
13:00 | 14:00 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 100 | 4200 | 4000 | 2800
14:00 | 15:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 99 | 4337 | 4137 | 2897
15:00 | 16:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 97 | 3877 | 3677 | 2574
16:00 | 17:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3454 | 3254 | 2278
17:00 | 18:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 99 | 3696 | 3496 | 2447
18:00 | 19:00 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3497 | 3297 | 2308
19:00 | 20:00 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 2608 | 2408 | 1686
20:00 | 21:00 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 2440 | 2240 | 1568
21:00 | 22:00 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 2345 | 2145 | 1502
22:00 | 23:00 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 99 | 2842 | 2642 | 1849
23:00 | 00:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 99 | 3248 | 3048 | 2134

## SRO borders-imports
SUBMISSION DATE: | 21.08.2026
BUSINESS DATE: | 23.08.2026
DA CC Remedial Actions
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC BG-RO
00:00 | 01:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3844 | 3644 | 2551
01:00 | 02:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 98 | 3844 | 3644 | 2551
02:00 | 03:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 92 | 3752 | 3552 | 2486
03:00 | 04:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 88 | 3735 | 3535 | 2474
04:00 | 05:00 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | 87 | 3733 | 3533 | 2473
05:00 | 06:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 85 | 3729 | 3529 | 2470
06:00 | 07:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 90 | 3745 | 3545 | 2482
07:00 | 08:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 98 | 3532 | 3332 | 2332
08:00 | 09:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 2863 | 2663 | 1864
09:00 | 10:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 2724 | 2524 | 1767
10:00 | 11:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 3380 | 3180 | 2226
11:00 | 12:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 98 | 3817 | 3617 | 2532
12:00 | 13:00 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3251 | 3051 | 2136
13:00 | 14:00 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | 100 | 2805 | 2605 | 1824
14:00 | 15:00 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3295 | 3095 | 2166
15:00 | 16:00 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | 100 | 3575 | 3375 | 2362
16:00 | 17:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 97 | 3788 | 3588 | 2512
17:00 | 18:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 97 | 3831 | 3631 | 2542
18:00 | 19:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 94 | 3909 | 3709 | 2596
19:00 | 20:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 96 | 3823 | 3623 | 2536
20:00 | 21:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 96 | 3798 | 3598 | 2519
21:00 | 22:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 96 | 3831 | 3631 | 2542
22:00 | 23:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 93 | 3891 | 3691 | 2584
23:00 | 00:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 90 | 3881 | 3681 | 2577

## SRO borders-exports RAs
SUBMISSION DATE: | 21.08.2026
BUSINESS DATE: | 23.08.2026
DA CC Remedial Actions
Initial CCC
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00008 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00009 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00017 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
NonCostly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
NonCostly Step 5
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
Costly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
RROVI31 _generator | RO_RA_00105 | costly_ra | 197 | 38 | [14 empty] | 1
RIERN22 _generator | RO_RA_00110 | costly_ra | 116 | 1 | 1 | [9 empty] | 1 | 1
RPDF212 _generator | RO_RA_00115 | costly_ra | 0 | 0 | 51 | [9 empty] | 52 | 53 |  |  | 363 |  | 0
RVMAR_5 _generator | RO_RA_00116 | costly_ra | 50 | 50 | 50 | [9 empty] | 50 | 50 |  |  | 50 |  | 0
RGODI_5 _generator | RO_RA_00117 | costly_ra | 114 | 114 | 114 | [9 empty] | 114 | 114 |  |  | 114
RTOPV_5 _generator | RO_RA_00120 | costly_ra | 10 | 10 | 10 | [10 empty] | 0 |  |  | 10 |  | 10
RFMEP_5 _generator | RO_RA_00121 | costly_ra | 14 | 14 | 14 | [10 empty] | 0 |  |  | 14 |  | 14
RVLCE15 _generator | RO_RA_00122 | costly_ra | 55 | 55 | 55 | [9 empty] | 0 | 0 |  |  | 55 |  | 55
RVALD_5 _generator | RO_RA_00123 | costly_ra | 15 | 15 | 15 | [10 empty] | 0 |  |  | 15 |  | 15
RELAR_5 _generator | RO_RA_00124 | costly_ra | 10 | 10 | 10 | [10 empty] | 0 |  |  | 10 |  | 10
RAREF_5 _generator | RO_RA_00125 | costly_ra | 10 | 10 | 10 | [10 empty] | 0 |  |  | 10 |  | 10
RARGS_5 _generator | RO_RA_00126 | costly_ra | 31 | 31 | 31 | [10 empty] | 0 |  |  | 31 |  | 31
RALBE_5 _generator | RO_RA_00127 | costly_ra | 30 | 30 | 30 | [10 empty] | 0 |  |  | 30 |  | 30
RCERB_5 _generator | RO_RA_00128 | costly_ra | 15 | 15 | 15 | [10 empty] | 0 |  |  | 15 |  | 15
RVLCE25 _generator | RO_RA_00129 | costly_ra | 12 | 12 | 12 | [10 empty] | 0 |  |  | 12 |  | 12
RCLNG_5 _generator | RO_RA_00130 | costly_ra | 90 | 90 | 90 | [9 empty] | 0 | 0 |  |  | 90 |  | 90
RLOT212 _generator | RO_RA_00132 | costly_ra | 0 | 0 | 217 | [9 empty] | 158 | 136 |  |  | 0 |  | 0
RBRDS25 _generator | RO_RA_00133 | costly_ra | 0 | 0 | [14 empty] | 0 |  | 0
RSTUP_5 _generator | RO_RA_00134 | costly_ra | 45 | 45 | 45 | [13 empty] | 45 |  | 45
RDAIES5 _generator | RO_RA_00135 | costly_ra | 37 | 37 | 37 | [13 empty] | 37 |  | 37
RVILN_5 _generator | RO_RA_00136 | costly_ra | 46 | 46 | 46 | [13 empty] | 46 |  | 46
RRIUR15 _generator | RO_RA_00137 | costly_ra | 48 | 48 | 48 | [13 empty] | 48 |  | 48
RMARC_5 _generator | RO_RA_00138 | costly_ra | 39 | 39 | 39 | [9 empty] | 0 | 0 |  |  | 39 |  | 39
RIONE_5 _generator | RO_RA_00139 | costly_ra | 38 | 38 | 38 | [13 empty] | 38 |  | 38
RJIBL_5 _generator | RO_RA_00140 | costly_ra | 38 | 38 | 38 | [13 empty] | 38 |  | 38
RZAVI_5 _generator | RO_RA_00141 | costly_ra | 38 | 38 | 38 | [13 empty] | 38 |  | 38
RCHTU_5 _generator | RO_RA_00142 | costly_ra | 74 | 74 | 74 | [15 empty] | 74
RTRAI_5 _generator | RO_RA_00143 | costly_ra | 45 | 45 | 45 | [13 empty] | 45 |  | 45
RHGLOT5 _generator | RO_RA_00144 | costly_ra | 25 | 25 | 25 | [15 empty] | 25
RCHESJ5 _generator | RO_RA_00145 | costly_ra | 50 | 50 | 50 | [9 empty] | 0 | 0 |  |  | 0 |  | 50
RCHEAC5 _generator | RO_RA_00146 | costly_ra | 38 | 38 | 38 | [9 empty] | 0 | 0 |  |  | 0 |  | 38
RCHEST5 _generator | RO_RA_00147 | costly_ra | 26 | 26 | 26 | [9 empty] | 0 | 0 |  |  | 0 |  | 26
RCHEIO5 _generator | RO_RA_00148 | costly_ra | 53 | 53 | 53 | [9 empty] | 0 | 0 |  |  | 0 |  | 53
RCHDO_5 _generator | RO_RA_00149 | costly_ra | 53 | 53 | 53 | [9 empty] | 0 | 0 |  |  | 0 |  | 53
RFRUN_5 _generator | RO_RA_00150 | costly_ra | 53 | 53 | 53 | [9 empty] | 0 | 0 |  |  | 0 |  | 53
RCIZBI5 _generator | RO_RA_00151 | costly_ra | 53 | 53 | 53 | [9 empty] | 0 | 0 |  |  | 0 |  | 53
RRUSA_5 _generator | RO_RA_00152 | costly_ra | 53 | 53 | 53 | [9 empty] | 0 | 0 |  |  | 0 |  | 53
RHCORN5 _generator | RO_RA_00153 | costly_ra | 59 | 59 | 59 | [13 empty] | 0 |  | 59
RSTEJ_5 _generator | RO_RA_00158 | costly_ra | 0 |  | 0 | [9 empty] | 0 | 0 |  |  | 79
RVADU_5 _generator | RO_RA_00160 | costly_ra | 0 | 67 | 0 | [15 empty] | 67
RIZVO_5 _generator | RO_RA_00161 | costly_ra | 0 | 9 | 0 | [13 empty] | 0 |  | 0
RDUMB_5 _generator | RO_RA_00162 | costly_ra | 0 | 23 | 0 | [9 empty] | 0 | 0 |  |  | 0 |  | 0
RCOST_5 _generator | RO_RA_00163 | costly_ra | 0 | 24 | 0 | [9 empty] | 0 | 0 |  |  | 0 |  | 0
RBUHU_5 _generator | RO_RA_00164 | costly_ra | 13 | 13 | 0 | [13 empty] | 0 |  | 0
RRACO_5 _generator | RO_RA_00165 | costly_ra | 23 | 23 | 0 | [9 empty] | 0 | 0 |  |  | 0 |  | 0
RGARL_5 _generator | RO_RA_00166 | costly_ra | 23 | 23 | 0 | [9 empty] | 0 | 0 |  |  | 0 |  | 0
RLILI_5 _generator | RO_RA_00167 | costly_ra | 23 | 23 | 0 | [9 empty] | 0 | 0 |  |  | 0 |  | 0
RBACS_5 _generator | RO_RA_00168 | costly_ra | 0 | 98 | 0 | [9 empty] | 0 | 0 |  |  | 0 |  | 0
RFARA_5 _generator | RO_RA_00169 | costly_ra | 30 | 30 | 0 | [9 empty] | 0 | 0 |  |  | 0 |  | 0
RSISC_5 _generator | RO_RA_00170 | costly_ra | 0 | 44 | 0 | [9 empty] | 0 | 0 |  |  | 0 |  | 0
RMARA_5 _generator | RO_RA_00171 | costly_ra | 46 | 46 | 0 | [9 empty] | 0 | 0 |  |  | 0 |  | 0
RTECU_5 _generator | RO_RA_00172 | costly_ra | 34 | 34 | 0 | [9 empty] | 0 | 0 |  |  | 0 |  | 34
RMARI22 _generator | RO_RA_00173 | costly_ra | 217 | 135 | 0 | [9 empty] | 217 | 217 |  |  | 217 |  | 217
RSEBE_5 _generator | RO_RA_00176 | costly_ra | 0 | 0 | 0 | [9 empty] | 55 | 55 |  |  | 55 |  | 55
RREME_5 _generator | RO_RA_00178 | costly_ra | 96 | 96 | [10 empty] | 96 | 96 |  |  | 96 |  | 96
RMUNT_5 _generator | RO_RA_00179 | costly_ra | 58 | 58 | [10 empty] | 58 | 58 |  |  | 58 |  | 58
RRETE22 _generator | RO_RA_00180 | costly_ra | 0 | 0 | [10 empty] | 222 | 222 |  |  | 0 |  | 0
RRETE_5 _generator | RO_RA_00181 | costly_ra | 0 | 0 | 20 | [9 empty] | 20 | 20 |  |  | 0 |  | 0
RCIRNA5 _generator | RO_RA_00182 | costly_ra | 0 | 0 | 0 | [9 empty] | 29 | 29 |  |  | 0 |  | 0
RCIRNB5 _generator | RO_RA_00183 | costly_ra | 0 | 0 | 0 | [9 empty] | 27 | 27 |  |  | 0 |  | 0
RHATE_5 _generator | RO_RA_00184 | costly_ra | 0 | 0 | 0 | [9 empty] | 52 | 52 |  |  | 0 |  | 0
RSTEJ25 _generator | RO_RA_00159 | costly_ra |  | 32 | [16 empty] | 32
RGILC22 _generator | RO_RA_00175 | costly_ra |  | 0 | 0 | [9 empty] | 150 | 150 |  |  | 150 |  | 131
RUCEA15 _generator | RO_RA_00156 | costly_ra |  |  | 49 | [9 empty] | 49 | 0 |  |  | 0 |  | 0
RCIRT_5 _generator | RO_RA_00157 | costly_ra |  |  | 54 | [9 empty] | 54 |  |  |  | 0 |  | 0
RBRAZ41 _generator | RO_RA_00111 | costly_ra | [12 empty] | 1 | 1
RBRZ241 _generator | RO_RA_00112 | costly_ra | [12 empty] | 1 | 1
RBRAZ22 _generator | RO_RA_00113 | costly_ra | [12 empty] | 1 | 1
RUCEA25 _generator | RO_RA_00155 | costly_ra | [12 empty] | 32 | 0 |  |  | 0 |  | 0
RSUGA22 _generator | RO_RA_00174 | costly_ra | [12 empty] | 150 | 150 |  |  | 150
RIAZUA5 _generator | RO_RA_00177 | costly_ra | [12 empty] | 71 | 71
RLOTR22 _generator | RO_RA_00131 | costly_ra | [13 empty] | 170
RROV641 _generator | RO_RA_00106 | costly_ra | [16 empty] | 1 |  | 298
RFAGA_5 _generator | RO_RA_00154 | costly_ra | [16 empty] | 0 |  | 0

## SRO borders-imports RAs
SUBMISSION DATE: | 21.08.2026
BUSINESS DATE: | 23.08.2026
DA CC Remedial Actions
Initial CCC
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful | helpful | helpful | notApplied | notApplied | notApplied | [5 empty] | helpful | notApplied | helpful | notApplied |  | helpful | [5 empty] | notApplied
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00008 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | [5 empty] | notApplied | notApplied | notApplied | notApplied |  | notApplied | [5 empty] | notApplied
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00009 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | [5 empty] | notApplied | notApplied | notApplied | notApplied |  | notApplied | [5 empty] | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | [5 empty] | helpful | helpful | helpful | helpful |  | helpful | [5 empty] | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00017 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | [5 empty] | notApplied | notApplied | notApplied | notApplied |  | notApplied | [5 empty] | notApplied
PRA 110 kV S4 | RO_RA_00003 | topological | [13 empty] | notApplied |  | notApplied
NonCostly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological_ra | [11 empty] | applied
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst_ra | [11 empty] | applied
NonCostly Step 5
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
Costly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
RFMEP_5 _generator | RO_RA_00121 | costly_ra | [8 empty] | 0
RVLCE15 _generator | RO_RA_00122 | costly_ra | [8 empty] | 0
RVALD_5 _generator | RO_RA_00123 | costly_ra | [8 empty] | 0
RARGS_5 _generator | RO_RA_00126 | costly_ra | [8 empty] | 0
RALBE_5 _generator | RO_RA_00127 | costly_ra | [8 empty] | 0
RCERB_5 _generator | RO_RA_00128 | costly_ra | [8 empty] | 0
RCLNG_5 _generator | RO_RA_00130 | costly_ra | [8 empty] | 0
RCHESJ5 _generator | RO_RA_00145 | costly_ra | [8 empty] | 0
RCHEAC5 _generator | RO_RA_00146 | costly_ra | [8 empty] | 0
RCHEST5 _generator | RO_RA_00147 | costly_ra | [8 empty] | 0
RCHEIO5 _generator | RO_RA_00148 | costly_ra | [8 empty] | 0
RCHDO_5 _generator | RO_RA_00149 | costly_ra | [8 empty] | 53
RFRUN_5 _generator | RO_RA_00150 | costly_ra | [8 empty] | 53
RCIZBI5 _generator | RO_RA_00151 | costly_ra | [8 empty] | 21
RRUSA_5 _generator | RO_RA_00152 | costly_ra | [8 empty] | 53
RHCORN5 _generator | RO_RA_00153 | costly_ra | [8 empty] | 0
RUCEA25 _generator | RO_RA_00155 | costly_ra | [8 empty] | 0
RUCEA15 _generator | RO_RA_00156 | costly_ra | [8 empty] | 0
RCIRT_5 _generator | RO_RA_00157 | costly_ra | [8 empty] | 0
RVADU_5 _generator | RO_RA_00160 | costly_ra | [8 empty] | 0
RIZVO_5 _generator | RO_RA_00161 | costly_ra | [8 empty] | 0
RDUMB_5 _generator | RO_RA_00162 | costly_ra | [8 empty] | 0
RCOST_5 _generator | RO_RA_00163 | costly_ra | [8 empty] | 0
RBUHU_5 _generator | RO_RA_00164 | costly_ra | [8 empty] | 0
RRACO_5 _generator | RO_RA_00165 | costly_ra | [8 empty] | 0
RGARL_5 _generator | RO_RA_00166 | costly_ra | [8 empty] | 0
RLILI_5 _generator | RO_RA_00167 | costly_ra | [8 empty] | 0
RBACS_5 _generator | RO_RA_00168 | costly_ra | [8 empty] | 0
RFARA_5 _generator | RO_RA_00169 | costly_ra | [8 empty] | 0
RSISC_5 _generator | RO_RA_00170 | costly_ra | [8 empty] | 0
RMARA_5 _generator | RO_RA_00171 | costly_ra | [8 empty] | 0
RTECU_5 _generator | RO_RA_00172 | costly_ra | [8 empty] | 0
RSEBE_5 _generator | RO_RA_00176 | costly_ra | [8 empty] | 0
RRETE_5 _generator | RO_RA_00181 | costly_ra | [8 empty] | 0
RCIRNA5 _generator | RO_RA_00182 | costly_ra | [8 empty] | 0
RCIRNB5 _generator | RO_RA_00183 | costly_ra | [8 empty] | 0
RHATE_5 _generator | RO_RA_00184 | costly_ra | [8 empty] | 0