## 0030
Detailed results
Generated at: | 21/08/2026 21:49:33
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3844.29
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1572 | 1570 | 2 | 100 | -1107 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1572 | 1570 | 2 | 100 | -1107 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1552 | 1570 | -18 | 99 | -1092 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1552 | 1570 | -18 | 99 | -1092 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1545 | 1570 | -25 | 98 | -1086 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1503 | 1570 | -67 | 96 | -1057 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 955 | 999 | -44 | 96 | 357 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1496 | 1570 | -74 | 95 | -1052 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1491 | 1570 | -79 | 95 | -1049 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1475 | 1570 | -95 | 94 | -1037 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1464 | 1570 | -106 | 93 | -1031 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1447 | 1570 | -123 | 92 | -1019 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1425 | 1570 | -145 | 91 | -1000 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1409 | 1570 | -161 | 90 | -991 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1385 | 1570 | -185 | 88 | -976 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1297 | 1500 | -203 | 86 | 936 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1210 | 1500 | -290 | 81 | 871 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1399 | 1740 | -341 | 80 | -927 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1454 | 1890 | -436 | 77 | 1028 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1454 | 1890 | -436 | 77 | 1028 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1319 | 1740 | -421 | 76 | -876 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1454 | 1920 | -466 | 76 | -1004 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1454 | 1920 | -466 | 76 | -1004 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1289 | 1740 | -451 | 74 | -857 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1287 | 1740 | -453 | 74 | -854 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 554 | 750 | -196 | 74 | 219 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1286 | 1740 | -454 | 74 | -856 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1264 | 1740 | -476 | 73 | -842 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1262 | 1740 | -478 | 73 | -841 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1246 | 1740 | -494 | 72 | -831 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1246 | 1740 | -494 | 72 | -831 | AC
Base case | Base case | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1239 | 1740 | -501 | 71 | -827 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1229 | 1740 | -511 | 71 | -822 | AC

## 0130
Detailed results
Generated at: | 21/08/2026 21:49:33
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3843.71
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1007 | 999 | 7 | 101 | 374 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1540 | 1570 | -30 | 98 | -1080 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1540 | 1570 | -30 | 98 | -1080 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1525 | 1570 | -45 | 97 | -1066 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1525 | 1570 | -45 | 97 | -1068 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1525 | 1570 | -45 | 97 | -1068 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1570 | -92 | 94 | -1033 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1465 | 1570 | -105 | 93 | -1026 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1461 | 1570 | -109 | 93 | -1023 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1454 | 1570 | -116 | 93 | -1016 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1432 | 1570 | -138 | 91 | -1004 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1575 | 1740 | -165 | 91 | -1033 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1413 | 1570 | -157 | 90 | -990 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1347 | 1500 | -153 | 90 | 972 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1401 | 1570 | -169 | 89 | -978 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1367 | 1570 | -203 | 87 | -956 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1358 | 1570 | -212 | 86 | -952 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1484 | 1740 | -256 | 85 | -976 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1453 | 1740 | -287 | 83 | -953 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1250 | 1500 | -250 | 83 | 900 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1447 | 1740 | -293 | 83 | -953 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1445 | 1740 | -295 | 83 | -953 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1427 | 1740 | -313 | 82 | -941 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1406 | 1740 | -334 | 81 | -930 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1405 | 1740 | -335 | 81 | -929 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1405 | 1740 | -335 | 81 | -929 | AC
Base case | Base case | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1397 | 1740 | -343 | 80 | -925 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1481 | 1890 | -409 | 78 | 1047 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1481 | 1890 | -409 | 78 | 1047 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1353 | 1740 | -387 | 78 | -899 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1481 | 1920 | -439 | 77 | -1022 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1481 | 1920 | -439 | 77 | -1022 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1171 | 1600 | -429 | 73 | -767 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1401 | 2000 | -599 | 70 | -882 | AC

## 0230
Detailed results
Generated at: | 21/08/2026 21:49:34
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3752.18
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 982 | 999 | -17 | 98 | 367 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 972 | 999 | -27 | 97 | 361 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1570 | -122 | 92 | -1015 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1570 | -122 | 92 | -1015 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1438 | 1570 | -132 | 92 | -999 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1430 | 1570 | -140 | 91 | -1000 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1430 | 1570 | -140 | 91 | -1000 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1383 | 1570 | -187 | 88 | -964 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1371 | 1570 | -199 | 87 | -957 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1366 | 1570 | -204 | 87 | -955 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1358 | 1570 | -212 | 86 | -948 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1486 | 1740 | -254 | 85 | -980 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1336 | 1570 | -234 | 85 | -937 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1319 | 1570 | -251 | 84 | -923 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1302 | 1570 | -268 | 83 | -909 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1240 | 1500 | -260 | 83 | 898 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1407 | 1740 | -333 | 81 | -929 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1259 | 1570 | -311 | 80 | -879 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1257 | 1570 | -313 | 80 | -883 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1383 | 1740 | -357 | 80 | -910 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1379 | 1740 | -361 | 79 | -912 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1496 | 1890 | -394 | 79 | 1058 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1496 | 1890 | -394 | 79 | 1058 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1377 | 1740 | -363 | 79 | -911 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1496 | 1920 | -424 | 78 | -1033 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1496 | 1920 | -424 | 78 | -1033 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1356 | 1740 | -384 | 78 | -897 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1164 | 1500 | -336 | 78 | 842 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1336 | 1740 | -404 | 77 | -889 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1333 | 1740 | -407 | 77 | -886 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1333 | 1740 | -407 | 77 | -886 | AC
Base case | Base case | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1324 | 1740 | -416 | 76 | -881 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1297 | 1740 | -443 | 75 | -859 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 530 | 750 | -220 | 71 | 209 | AC

## 0330
Detailed results
Generated at: | 21/08/2026 21:49:34
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3734.71
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1009 | 999 | 10 | 101 | 374 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 995 | 999 | -4 | 100 | 367 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1555 | 1740 | -185 | 89 | -1015 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1378 | 1570 | -192 | 88 | -983 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1378 | 1570 | -192 | 88 | -983 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1570 | -205 | 87 | -968 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1570 | -209 | 87 | -970 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1570 | -209 | 87 | -970 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1472 | 1740 | -268 | 85 | -963 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1311 | 1570 | -259 | 84 | -932 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1448 | 1740 | -292 | 83 | -944 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1246 | 1500 | -254 | 83 | 901 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1440 | 1740 | -300 | 83 | -944 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1298 | 1570 | -272 | 83 | -925 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1437 | 1740 | -303 | 83 | -943 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1294 | 1570 | -276 | 82 | -922 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1289 | 1570 | -281 | 82 | -918 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1418 | 1740 | -322 | 82 | -930 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1264 | 1570 | -306 | 81 | -904 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1520 | 1890 | -370 | 80 | 1075 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1520 | 1890 | -370 | 80 | 1075 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1395 | 1740 | -345 | 80 | -920 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1395 | 1740 | -345 | 80 | -920 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1395 | 1740 | -345 | 80 | -920 | AC
Base case | Base case | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1386 | 1740 | -354 | 80 | -915 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1246 | 1570 | -324 | 79 | -890 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1520 | 1920 | -400 | 79 | -1048 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1520 | 1920 | -400 | 79 | -1048 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1230 | 1570 | -340 | 78 | -879 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1168 | 1500 | -332 | 78 | 843 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1348 | 1740 | -392 | 78 | -886 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1188 | 1570 | -382 | 76 | -851 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1187 | 1570 | -383 | 76 | -847 | AC

## 0430
Detailed results
Generated at: | 21/08/2026 21:49:34
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3733.17
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Nadab-Bekescsaba/[RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 984 | 999 | -15 | 98 | 367 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 969 | 999 | -30 | 97 | 362 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1360 | 1570 | -210 | 87 | -942 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1360 | 1570 | -210 | 87 | -942 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1506 | 1740 | -234 | 87 | -994 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1338 | 1570 | -232 | 85 | -920 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1335 | 1570 | -235 | 85 | -921 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1335 | 1570 | -235 | 85 | -921 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1569 | 1890 | -321 | 83 | 1109 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1569 | 1890 | -321 | 83 | 1109 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1427 | 1740 | -313 | 82 | -944 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1284 | 1570 | -286 | 82 | -883 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1569 | 1920 | -351 | 82 | -1081 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1569 | 1920 | -351 | 82 | -1081 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1273 | 1570 | -297 | 81 | -878 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1269 | 1570 | -301 | 81 | -876 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1401 | 1740 | -339 | 81 | -926 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1401 | 1740 | -339 | 80 | -929 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1399 | 1740 | -341 | 80 | -927 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1259 | 1570 | -311 | 80 | -868 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1377 | 1740 | -363 | 79 | -914 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1242 | 1570 | -328 | 79 | -860 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1361 | 1740 | -379 | 78 | -905 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1227 | 1570 | -343 | 78 | -846 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1359 | 1740 | -381 | 78 | -904 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1359 | 1740 | -381 | 78 | -904 | AC
Base case | Base case | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1351 | 1740 | -389 | 78 | -899 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1216 | 1570 | -354 | 77 | -834 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1161 | 1500 | -339 | 77 | 839 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1323 | 1740 | -417 | 76 | -883 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1297 | 1722 | -425 | 75 | 913 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1290 | 1722 | -432 | 75 | 905 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1170 | 1570 | -400 | 75 | -808 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1148 | 1570 | -422 | 73 | -787 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1248 | 1722 | -474 | 72 | 877 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1246 | 1722 | -476 | 72 | 870 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1242 | 1722 | -480 | 72 | 873 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1236 | 1722 | -486 | 72 | 868 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1075 | 1500 | -425 | 72 | 776 | AC
Base case | Base case | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1213 | 1722 | -509 | 70 | 852 | AC

## 0530
Detailed results
Generated at: | 21/08/2026 21:49:34
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3728.58
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 974 | 999 | -25 | 98 | 365 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 969 | 999 | -31 | 97 | 363 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1570 | -205 | 87 | -943 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1570 | -205 | 87 | -943 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1336 | 1570 | -234 | 85 | -919 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1336 | 1570 | -234 | 85 | -919 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1335 | 1570 | -235 | 85 | -916 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1607 | 1890 | -283 | 85 | 1136 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1607 | 1890 | -283 | 85 | 1136 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1457 | 1740 | -283 | 84 | -966 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1607 | 1920 | -313 | 84 | -1106 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1607 | 1920 | -313 | 84 | -1106 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1282 | 1570 | -288 | 82 | -880 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1273 | 1570 | -297 | 81 | -876 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1269 | 1570 | -301 | 81 | -874 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1251 | 1570 | -319 | 80 | -860 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1380 | 1740 | -360 | 79 | -916 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1244 | 1570 | -326 | 79 | -858 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1228 | 1570 | -342 | 78 | -845 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1354 | 1740 | -386 | 78 | -901 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1353 | 1740 | -387 | 78 | -900 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1352 | 1740 | -388 | 78 | -898 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1214 | 1570 | -356 | 77 | -831 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1329 | 1740 | -411 | 76 | -885 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1314 | 1722 | -408 | 76 | 926 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1320 | 1740 | -420 | 76 | -881 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1136 | 1500 | -364 | 76 | 821 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1303 | 1722 | -419 | 76 | 916 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1313 | 1740 | -427 | 75 | -877 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1313 | 1740 | -427 | 75 | -877 | AC
Base case | Base case | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1305 | 1740 | -435 | 75 | -872 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1289 | 1722 | -433 | 75 | 906 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1295 | 1740 | -445 | 74 | -866 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1168 | 1570 | -402 | 74 | -804 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1143 | 1570 | -427 | 73 | -781 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1251 | 1722 | -471 | 73 | 881 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1247 | 1722 | -475 | 72 | 874 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1236 | 1722 | -486 | 72 | 869 | AC
Base case | Base case | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1220 | 1722 | -502 | 71 | 859 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1055 | 1500 | -445 | 70 | 762 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 526 | 750 | -224 | 70 | 210 | AC

## 0630
Detailed results
Generated at: | 21/08/2026 21:49:34
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3745.25
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 942 | 999 | -57 | 94 | 356 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 942 | 999 | -57 | 94 | 357 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1709 | 1890 | -181 | 90 | 1207 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1709 | 1890 | -181 | 90 | 1207 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1709 | 1920 | -211 | 89 | -1173 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1709 | 1920 | -211 | 89 | -1173 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1570 | -209 | 87 | -954 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1570 | -209 | 87 | -954 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1315 | 1570 | -255 | 84 | -918 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1315 | 1570 | -255 | 84 | -918 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1308 | 1570 | -262 | 83 | -913 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1258 | 1570 | -312 | 80 | -879 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1254 | 1570 | -316 | 80 | -876 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1250 | 1570 | -320 | 80 | -874 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1229 | 1570 | -341 | 78 | -860 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1344 | 1722 | -378 | 78 | 946 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1224 | 1570 | -346 | 78 | -855 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1341 | 1722 | -381 | 78 | 946 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1216 | 1570 | -354 | 77 | -850 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 578 | 750 | -172 | 77 | 236 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1327 | 1722 | -395 | 77 | 934 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1338 | 1740 | -402 | 77 | -899 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1191 | 1570 | -379 | 76 | -829 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1268 | 1722 | -454 | 74 | 894 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1156 | 1570 | -414 | 74 | -803 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1272 | 1740 | -468 | 73 | -856 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1256 | 1722 | -466 | 73 | 882 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1261 | 1740 | -479 | 72 | -849 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1243 | 1722 | -479 | 72 | 875 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1253 | 1740 | -487 | 72 | -844 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1077 | 1500 | -423 | 72 | 777 | AC
Base case | Base case | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1235 | 1722 | -487 | 72 | 871 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1245 | 1740 | -495 | 72 | -839 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1226 | 1722 | -496 | 71 | 866 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1112 | 1570 | -458 | 71 | -773 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1225 | 1740 | -515 | 70 | -827 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1225 | 1740 | -515 | 70 | -827 | AC

## 0730
Detailed results
Generated at: | 21/08/2026 21:49:35
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3531.83
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1843 | 1890 | -47 | 98 | 1308 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1843 | 1890 | -47 | 98 | 1308 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1843 | 1920 | -77 | 96 | -1269 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1843 | 1920 | -77 | 96 | -1269 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 625 | 750 | -125 | 83 | 253 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1394 | 1722 | -328 | 81 | 985 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1382 | 1722 | -340 | 80 | 975 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1357 | 1722 | -365 | 79 | 958 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1217 | 1570 | -353 | 78 | -856 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1310 | 1722 | -412 | 76 | 920 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1298 | 1722 | -424 | 75 | 916 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1292 | 1722 | -430 | 75 | 913 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 735 | 999 | -264 | 74 | 285 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1266 | 1722 | -456 | 74 | 895 | AC
Base case | Base case | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1259 | 1722 | -463 | 73 | 889 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1146 | 1570 | -424 | 73 | -808 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1146 | 1570 | -424 | 73 | -808 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 713 | 999 | -286 | 71 | 276 | AC

## 0830
Detailed results
Generated at: | 21/08/2026 21:49:35
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2863
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 2 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 4 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 1 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 1 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 1 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 1 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 1 | 21 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 1 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 9 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 2 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 16 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 28 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 7 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 10 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 11 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 8 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 9 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 8 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 13 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1339 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1339 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1885 | 1920 | -35 | 98 | -1298 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1885 | 1920 | -35 | 98 | -1298 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 601 | 750 | -149 | 80 | 244 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1287 | 1722 | -435 | 75 | 908 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1278 | 1722 | -444 | 74 | 899 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1240 | 1722 | -482 | 72 | 874 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1358 | 1920 | -562 | 71 | -944 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1358 | 1920 | -562 | 71 | -944 | AC

## 0930
Detailed results
Generated at: | 21/08/2026 21:49:35
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2724
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1339 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1339 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1885 | 1920 | -35 | 98 | -1299 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1885 | 1920 | -35 | 98 | -1299 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1369 | 1920 | -551 | 71 | -953 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1369 | 1920 | -551 | 71 | -953 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1214 | 1722 | -508 | 71 | 854 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1207 | 1722 | -515 | 70 | 846 | AC

## 1030
Detailed results
Generated at: | 21/08/2026 21:49:35
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3380
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1338 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1338 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1885 | 1920 | -35 | 98 | -1297 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1885 | 1920 | -35 | 98 | -1297 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1317 | 1722 | -405 | 76 | 925 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1312 | 1722 | -410 | 76 | 919 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 554 | 750 | -196 | 74 | 224 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1255 | 1722 | -467 | 73 | 873 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1246 | 1722 | -476 | 72 | 872 | AC

## 1130
Detailed results
Generated at: | 21/08/2026 21:49:35
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3817
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1542 | 1570 | -28 | 98 | -1100 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1542 | 1570 | -28 | 98 | -1100 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1570 | -94 | 94 | -1052 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1465 | 1570 | -105 | 93 | -1044 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1465 | 1570 | -105 | 93 | -1044 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1452 | 1570 | -118 | 92 | -1035 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1570 | -127 | 92 | -1030 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1441 | 1570 | -129 | 92 | -1028 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1425 | 1570 | -145 | 91 | -1016 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1416 | 1570 | -154 | 90 | -1011 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1402 | 1570 | -168 | 89 | -1001 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1675 | 1890 | -215 | 89 | 1190 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1675 | 1890 | -215 | 89 | 1190 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1675 | 1920 | -245 | 87 | -1158 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1675 | 1920 | -245 | 87 | -1158 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1364 | 1570 | -206 | 87 | -973 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1345 | 1570 | -225 | 86 | -959 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 823 | 999 | -176 | 82 | 317 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 823 | 999 | -176 | 82 | 316 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1273 | 1570 | -297 | 81 | -908 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1308 | 1722 | -414 | 76 | 917 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1304 | 1722 | -418 | 76 | 911 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1258 | 1722 | -464 | 73 | 874 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1090 | 1500 | -410 | 73 | 782 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1249 | 1722 | -473 | 73 | 872 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1231 | 1722 | -491 | 71 | 863 | AC

## 1230
Detailed results
Generated at: | 21/08/2026 21:49:35
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3251.33
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Rosiori-Mukacevo/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1571 | 1570 | 1 | 100 | -1115 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1000 | 999 | 1 | 100 | 375 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1565 | 1570 | -5 | 100 | -1113 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1565 | 1570 | -5 | 100 | -1113 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1546 | 1570 | -24 | 98 | -1100 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1546 | 1570 | -24 | 98 | -1100 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1538 | 1570 | -32 | 98 | -1092 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1528 | 1570 | -42 | 97 | -1084 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1521 | 1570 | -49 | 97 | -1082 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1516 | 1570 | -54 | 97 | -1078 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1486 | 1570 | -84 | 95 | -1059 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1631 | 1740 | -109 | 94 | -1079 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1462 | 1570 | -108 | 93 | -1040 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1453 | 1570 | -117 | 93 | -1033 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1379 | 1500 | -121 | 92 | 990 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1438 | 1570 | -132 | 92 | -1023 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1570 | -144 | 91 | -1013 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1503 | 1740 | -237 | 86 | -1000 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1481 | 1740 | -259 | 85 | -983 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1470 | 1740 | -270 | 84 | -979 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1451 | 1740 | -289 | 83 | -969 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1448 | 1740 | -292 | 83 | -965 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1244 | 1500 | -256 | 83 | 892 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1312 | 1600 | -288 | 82 | -867 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1415 | 1740 | -325 | 81 | -947 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1415 | 1740 | -325 | 81 | -947 | AC
Base case | Base case | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1408 | 1740 | -332 | 81 | -943 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1404 | 1740 | -336 | 81 | -941 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1614 | 2000 | -386 | 81 | -1032 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1334 | 1740 | -406 | 77 | -898 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1481 | 2000 | -519 | 74 | -974 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RO] [DIR] OHL 400 kV Rosiori-Gadalin | RROSI41 RGAD241 1 | 1063 | 1500 | -437 | 71 | 707 | AC

## 1330
Detailed results
Generated at: | 21/08/2026 21:49:35
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2805.5
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Nadab-Bekescsaba/[RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1059 | 999 | 60 | 106 | 389 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1010 | 999 | 11 | 101 | 375 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1739 | 1740 | -1 | 100 | -1135 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1600 | 1740 | -140 | 92 | -1052 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1578 | 1740 | -162 | 91 | -1035 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1555 | 1740 | -185 | 89 | -1024 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1545 | 1740 | -195 | 89 | -1018 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1536 | 1740 | -204 | 88 | -1014 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1510 | 1740 | -230 | 87 | -999 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1510 | 1740 | -230 | 87 | -999 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1570 | -209 | 87 | -963 | AC
Base case | Base case | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1503 | 1740 | -237 | 86 | -995 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1288 | 1500 | -212 | 86 | 924 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1490 | 1740 | -250 | 86 | -988 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1712 | 2000 | -288 | 86 | -1076 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1333 | 1570 | -237 | 85 | -942 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1333 | 1570 | -237 | 85 | -945 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1333 | 1570 | -237 | 85 | -945 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1357 | 1600 | -243 | 85 | -888 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1328 | 1570 | -242 | 85 | -942 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1328 | 1570 | -242 | 85 | -942 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1324 | 1570 | -246 | 84 | -937 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1306 | 1570 | -264 | 83 | -926 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1300 | 1570 | -270 | 83 | -922 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1272 | 1570 | -298 | 81 | -904 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1404 | 1740 | -336 | 81 | -936 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1249 | 1570 | -321 | 80 | -885 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1245 | 1570 | -325 | 79 | -883 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1226 | 1570 | -344 | 78 | -869 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1223 | 1570 | -347 | 78 | -867 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1545 | 2000 | -455 | 77 | -1007 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1147 | 1500 | -353 | 76 | 823 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RO] [DIR] OHL 400 kV Rosiori-Gadalin | RROSI41 RGAD241 1 | 1130 | 1500 | -370 | 75 | 744 | AC

## 1430
Detailed results
Generated at: | 21/08/2026 21:49:35
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3295.09
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Rosiori-Mukacevo/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1125 | 999 | 126 | 113 | 413 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1081 | 999 | 82 | 108 | 400 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1803 | 1740 | 63 | 104 | -1170 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1575 | 1570 | 5 | 100 | -1116 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1550 | 1570 | -20 | 99 | -1100 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1550 | 1570 | -20 | 99 | -1100 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1541 | 1570 | -29 | 98 | -1094 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1541 | 1570 | -29 | 98 | -1094 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1538 | 1570 | -32 | 98 | -1088 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1535 | 1570 | -35 | 98 | -1087 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1516 | 1570 | -54 | 97 | -1076 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1511 | 1570 | -59 | 96 | -1072 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1661 | 1740 | -79 | 95 | -1086 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1420 | 1500 | -80 | 95 | 1020 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1570 | -92 | 94 | -1052 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1636 | 1740 | -104 | 94 | -1067 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1619 | 1740 | -121 | 93 | -1061 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1451 | 1570 | -119 | 92 | -1031 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1446 | 1570 | -124 | 92 | -1026 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1600 | 1740 | -140 | 92 | -1049 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1597 | 1740 | -143 | 92 | -1049 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1428 | 1570 | -142 | 91 | -1015 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1418 | 1570 | -152 | 90 | -1006 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1564 | 1740 | -176 | 90 | -1031 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1564 | 1740 | -176 | 90 | -1031 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1436 | 1600 | -164 | 90 | -938 | AC
Base case | Base case | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1557 | 1740 | -183 | 89 | -1027 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1783 | 2000 | -217 | 89 | -1113 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1550 | 1740 | -190 | 89 | -1023 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1279 | 1500 | -221 | 85 | 916 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1468 | 1740 | -272 | 84 | -974 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1624 | 2000 | -376 | 81 | -1056 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RO] [DIR] OHL 400 kV Rosiori-Gadalin | RROSI41 RGAD241 1 | 1170 | 1500 | -330 | 78 | 766 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1141 | 1600 | -459 | 71 | -729 | AC

## 1530
Detailed results
Generated at: | 21/08/2026 21:49:36
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3574.82
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Nadab-Bekescsaba/[RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1095 | 999 | 96 | 110 | 404 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1053 | 999 | 54 | 105 | 392 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1739 | 1740 | -1 | 100 | -1136 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1600 | 1740 | -140 | 92 | -1052 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1423 | 1570 | -147 | 91 | -1008 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1419 | 1570 | -151 | 90 | -1006 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1419 | 1570 | -151 | 90 | -1006 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1572 | 1740 | -168 | 90 | -1032 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1552 | 1740 | -188 | 89 | -1023 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1395 | 1570 | -175 | 89 | -989 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1395 | 1570 | -175 | 89 | -989 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1418 | 1600 | -182 | 89 | -930 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1540 | 1740 | -200 | 88 | -1017 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1539 | 1740 | -201 | 88 | -1015 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1385 | 1570 | -185 | 88 | -980 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1373 | 1570 | -197 | 87 | -971 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1308 | 1500 | -192 | 87 | 939 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1368 | 1570 | -202 | 87 | -971 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1741 | 2000 | -259 | 87 | -1095 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1364 | 1570 | -206 | 87 | -967 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1504 | 1740 | -236 | 86 | -997 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1504 | 1740 | -236 | 86 | -997 | AC
Base case | Base case | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1497 | 1740 | -243 | 86 | -992 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1492 | 1740 | -248 | 86 | -990 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1332 | 1570 | -238 | 85 | -947 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1304 | 1570 | -266 | 83 | -926 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1301 | 1570 | -269 | 83 | -922 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1414 | 1740 | -326 | 81 | -943 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1273 | 1570 | -297 | 81 | -903 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1601 | 2000 | -399 | 80 | -1045 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1250 | 1570 | -320 | 80 | -886 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1175 | 1500 | -325 | 78 | 843 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RO] [DIR] OHL 400 kV Rosiori-Gadalin | RROSI41 RGAD241 1 | 1120 | 1500 | -380 | 75 | 738 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1352 | 1890 | -538 | 72 | 962 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1352 | 1890 | -538 | 72 | 962 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1352 | 1920 | -568 | 70 | -942 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1352 | 1920 | -568 | 70 | -942 | AC

## 1630
Detailed results
Generated at: | 21/08/2026 21:49:36
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3788.02
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 974 | 999 | -25 | 97 | 364 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1525 | 1570 | -45 | 97 | -1084 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 955 | 999 | -44 | 96 | 359 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1363 | 1570 | -207 | 87 | -963 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1363 | 1570 | -207 | 87 | -963 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1330 | 1570 | -240 | 85 | -938 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1600 | 1890 | -290 | 85 | 1138 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1600 | 1890 | -290 | 85 | 1138 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1456 | 1740 | -284 | 84 | -968 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1600 | 1920 | -320 | 83 | -1109 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1600 | 1920 | -320 | 83 | -1109 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1293 | 1570 | -277 | 82 | -911 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1284 | 1570 | -286 | 82 | -907 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1283 | 1570 | -287 | 82 | -906 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1253 | 1570 | -317 | 80 | -886 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1251 | 1570 | -319 | 80 | -882 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1224 | 1570 | -346 | 78 | -864 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1347 | 1740 | -393 | 77 | -899 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1207 | 1570 | -363 | 77 | -849 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1315 | 1722 | -407 | 76 | 918 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1309 | 1722 | -413 | 76 | 918 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1317 | 1740 | -423 | 76 | -879 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1315 | 1740 | -425 | 76 | -879 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1208 | 1600 | -392 | 76 | -801 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1297 | 1722 | -425 | 75 | 900 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1295 | 1722 | -427 | 75 | 904 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1307 | 1740 | -433 | 75 | -875 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1176 | 1570 | -394 | 75 | -828 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1290 | 1740 | -450 | 74 | -864 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1473 | 2000 | -527 | 74 | -1015 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1473 | 2000 | -527 | 74 | 1031 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1282 | 1740 | -458 | 74 | -859 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1262 | 1722 | -460 | 73 | 879 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1460 | 2000 | -540 | 73 | -1003 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1460 | 2000 | -540 | 73 | 1022 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1268 | 1740 | -472 | 73 | -851 | AC
Base case | Base case | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1259 | 1740 | -481 | 72 | -845 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1442 | 2000 | -558 | 72 | -931 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1228 | 1722 | -494 | 71 | 859 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1220 | 1722 | -502 | 71 | 850 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1108 | 1570 | -462 | 71 | -778 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1222 | 1740 | -518 | 70 | -823 | AC

## 1730
Detailed results
Generated at: | 21/08/2026 21:49:36
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3831.37
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1003 | 999 | 4 | 100 | 373 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 986 | 999 | -13 | 99 | 368 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1522 | 1570 | -48 | 97 | -1077 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1522 | 1570 | -48 | 97 | -1077 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1507 | 1570 | -63 | 96 | -1067 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1507 | 1570 | -63 | 96 | -1067 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1500 | 1570 | -70 | 96 | -1060 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1471 | 1570 | -99 | 94 | -1039 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1462 | 1570 | -108 | 93 | -1034 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1458 | 1570 | -112 | 93 | -1032 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1430 | 1570 | -140 | 91 | -1011 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1570 | -144 | 91 | -1011 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1405 | 1570 | -165 | 90 | -995 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1328 | 1500 | -172 | 89 | 956 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1570 | -182 | 88 | -982 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1376 | 1570 | -194 | 88 | -973 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1355 | 1570 | -215 | 86 | -957 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1445 | 1740 | -295 | 83 | -951 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1218 | 1500 | -282 | 81 | 875 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1270 | 1600 | -330 | 79 | -836 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1344 | 1740 | -396 | 77 | -888 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1308 | 1740 | -432 | 75 | -865 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1305 | 1740 | -435 | 75 | -864 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1294 | 1740 | -446 | 74 | -858 | AC
RO_CO_00003 | N-1 OHL 400 kV Sibiu Sud-Mintia | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1282 | 1740 | -458 | 74 | -850 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1264 | 1740 | -476 | 73 | -840 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1372 | 1890 | -518 | 73 | 976 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1372 | 1890 | -518 | 73 | 976 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1256 | 1740 | -484 | 72 | -835 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1256 | 1740 | -484 | 72 | -835 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1439 | 2000 | -561 | 72 | -919 | AC
Base case | Base case | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1249 | 1740 | -491 | 72 | -831 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1372 | 1920 | -548 | 71 | -955 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1372 | 1920 | -548 | 71 | -955 | AC

## 1830
Detailed results
Generated at: | 21/08/2026 21:49:36
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3908.72
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1775 | 1890 | -115 | 94 | 1262 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1775 | 1890 | -115 | 94 | 1262 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1775 | 1920 | -145 | 92 | -1226 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1775 | 1920 | -145 | 92 | -1226 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1324 | 1570 | -246 | 84 | -937 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1616 | 2000 | -384 | 81 | 1131 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1616 | 2000 | -384 | 81 | -1111 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1601 | 2000 | -399 | 80 | 1119 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1601 | 2000 | -399 | 80 | -1097 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1366 | 1722 | -356 | 79 | 952 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1356 | 1722 | -366 | 79 | 949 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1352 | 1722 | -370 | 79 | 942 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1349 | 1722 | -373 | 78 | 935 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 775 | 999 | -224 | 78 | 291 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 761 | 999 | -238 | 76 | 286 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1166 | 1570 | -404 | 74 | -820 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1166 | 1570 | -404 | 74 | -820 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1243 | 1722 | -479 | 72 | 863 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1234 | 1722 | -488 | 72 | 862 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1221 | 1722 | -501 | 71 | 855 | AC
Base case | Base case | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1216 | 1722 | -506 | 71 | 848 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1207 | 1722 | -515 | 70 | 839 | AC

## 1930
Detailed results
Generated at: | 21/08/2026 21:49:36
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3823.22
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1814 | 1890 | -76 | 96 | 1290 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1814 | 1890 | -76 | 96 | 1290 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1814 | 1920 | -106 | 94 | -1252 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1814 | 1920 | -106 | 94 | -1252 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1634 | 2000 | -366 | 82 | 1141 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1634 | 2000 | -366 | 82 | -1121 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1618 | 2000 | -382 | 81 | 1129 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1618 | 2000 | -382 | 81 | -1106 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1384 | 1722 | -338 | 80 | 962 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1373 | 1722 | -349 | 80 | 959 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1372 | 1722 | -350 | 80 | 953 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1369 | 1722 | -353 | 79 | 946 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1186 | 1570 | -384 | 76 | -826 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1263 | 1722 | -459 | 73 | 875 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1253 | 1722 | -469 | 73 | 873 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1239 | 1722 | -483 | 72 | 865 | AC
Base case | Base case | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1234 | 1722 | -488 | 72 | 859 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1227 | 1722 | -495 | 71 | 850 | AC

## 2030
Detailed results
Generated at: | 21/08/2026 21:49:36
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3797.74
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1819 | 1890 | -71 | 96 | 1293 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1819 | 1890 | -71 | 96 | 1293 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1819 | 1920 | -101 | 95 | -1255 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1819 | 1920 | -101 | 95 | -1255 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1665 | 2000 | -335 | 83 | 1164 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1665 | 2000 | -335 | 83 | -1143 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1651 | 2000 | -349 | 83 | 1153 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1651 | 2000 | -349 | 83 | -1129 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1397 | 1722 | -325 | 81 | 972 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1386 | 1722 | -336 | 80 | 968 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1383 | 1722 | -339 | 80 | 962 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1380 | 1722 | -342 | 80 | 954 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1257 | 1722 | -465 | 73 | 876 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1256 | 1722 | -466 | 73 | 870 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1248 | 1722 | -474 | 72 | 872 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1131 | 1570 | -439 | 72 | -785 | AC
Base case | Base case | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1238 | 1722 | -484 | 72 | 861 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1223 | 1722 | -499 | 71 | 848 | AC

## 2130
Detailed results
Generated at: | 21/08/2026 21:49:36
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3831.4
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1818 | 1890 | -72 | 96 | 1293 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1818 | 1890 | -72 | 96 | 1293 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1818 | 1920 | -102 | 95 | -1255 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1818 | 1920 | -102 | 95 | -1255 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1670 | 2000 | -330 | 83 | -1153 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1670 | 2000 | -330 | 83 | 1174 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1656 | 2000 | -344 | 83 | 1163 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1656 | 2000 | -344 | 83 | -1139 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1401 | 1722 | -321 | 81 | 980 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1391 | 1722 | -331 | 81 | 976 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1387 | 1722 | -335 | 81 | 970 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1383 | 1722 | -339 | 80 | 962 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1173 | 1570 | -397 | 75 | -806 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1260 | 1722 | -462 | 73 | 883 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1254 | 1722 | -468 | 73 | 874 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1251 | 1722 | -471 | 73 | 879 | AC
Base case | Base case | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1239 | 1722 | -483 | 72 | 867 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 710 | 999 | -290 | 71 | 269 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1222 | 1722 | -500 | 71 | 852 | AC

## 2230
Detailed results
Generated at: | 21/08/2026 21:49:36
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3890.59
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1764 | 1890 | -126 | 93 | 1246 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1764 | 1890 | -126 | 93 | 1246 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1764 | 1920 | -156 | 92 | -1210 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1764 | 1920 | -156 | 92 | -1210 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1418 | 1570 | -152 | 90 | -987 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 809 | 999 | -190 | 81 | 305 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 798 | 999 | -201 | 80 | 301 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1254 | 1570 | -316 | 80 | -860 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1254 | 1570 | -316 | 80 | -860 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1345 | 1722 | -377 | 78 | 937 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1558 | 2000 | -442 | 78 | 1090 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1558 | 2000 | -442 | 78 | -1071 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1336 | 1722 | -386 | 78 | 935 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1546 | 2000 | -454 | 77 | 1080 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1546 | 2000 | -454 | 77 | -1059 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1329 | 1722 | -393 | 77 | 926 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1328 | 1722 | -394 | 77 | 920 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1189 | 1570 | -381 | 76 | -808 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1150 | 1570 | -420 | 73 | -781 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1148 | 1570 | -422 | 73 | -779 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1139 | 1570 | -431 | 73 | -776 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1244 | 1722 | -478 | 72 | 864 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1122 | 1570 | -448 | 71 | -764 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1230 | 1722 | -492 | 71 | 859 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1107 | 1570 | -463 | 70 | -751 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1105 | 1570 | -465 | 70 | -750 | AC
Base case | Base case | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1209 | 1722 | -513 | 70 | 843 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1206 | 1722 | -516 | 70 | 844 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1206 | 1722 | -516 | 70 | 839 | AC

## 2330
Detailed results
Generated at: | 21/08/2026 21:49:36
Business day: | 2026-08-23
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3881.27
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1408 | 1570 | -162 | 90 | -965 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1408 | 1570 | -162 | 90 | -965 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1364 | 1570 | -206 | 87 | -930 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1364 | 1570 | -206 | 87 | -930 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1632 | 1890 | -258 | 86 | 1153 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1632 | 1890 | -258 | 86 | 1153 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1354 | 1570 | -216 | 86 | -921 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1632 | 1920 | -288 | 85 | -1123 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1632 | 1920 | -288 | 85 | -1123 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1318 | 1570 | -252 | 84 | -896 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1314 | 1570 | -256 | 84 | -894 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1305 | 1570 | -265 | 83 | -890 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 827 | 999 | -172 | 83 | 312 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 824 | 999 | -175 | 82 | 310 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1286 | 1570 | -284 | 82 | -877 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1280 | 1570 | -290 | 82 | -871 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1275 | 1570 | -295 | 81 | -868 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1252 | 1570 | -318 | 80 | -845 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1212 | 1570 | -358 | 77 | -823 | AC
RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1192 | 1570 | -378 | 76 | -803 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 539 | 750 | -211 | 72 | 217 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1221 | 1722 | -501 | 71 | 851 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1214 | 1722 | -508 | 70 | 849 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1057 | 1500 | -443 | 70 | 765 | AC